## Options Matrix Design Component
Energy Storage Participation in RPM
Options Matrix
Solution Options2
Number | Design Components1 | Priority (high/med/low) | Status Quo (Advanced Storage, Storage in PJM Today) | Status Quo (Resources in Capacity Market) | A | B | C | D | E | F | G | H | I
1 | Must offer requirement in day ahead market | low/medium | N/A (Batteries), Required (Storage) | All resources in Capacity market have a Must Offer Req in Day ahead | As other generation: must offer can be met through DA market, self schedule, or optional hydro optimizer | Self-scheduling | PJM optimization (e.g. pumped hydro) | Standard DA/RT, respecting max run time/max energy limits | same as conventional generation - with dynamic capability to determine cost | must offer req, market must match output req to be cap resource (10 hours)
2 | Minimum continuous electricity time capability | high | No Current Standard, Regulation ;market is hourly; cannot be out for XX mins, or else forfeit bid (Batteries), 10 hours (Storage) | 10 Hours | N/A, 330kWh to provide 100kW of UCAP (Proposed as Minimum Energy Capacity) | 1 hour | keep current products - limited, extended summer consistent with shortest duration of current DR products | 10 hours | 15 mins/shorter than 1 hour | 4 hours | 6 hours
3 | Minimum continuous electricity production capability | low/medium | Continuous Capability for a certain period, 0.1 MW for existing resources (Batteries and Storage) | Continuous Capability for a certain period, 0.1 MW for existing resources | Solution Options2 A: 100kW; Solution Options2 B: status quo
4 | Test requirements | medium |  | - 1-2 hours based on resource type, Steam 2 hrs, Hydro 1 hr - Qualifying test - Seasonal test - Equivalent to duration | Solution Options2 A: Option A to verify power rating. Once per year, full charge/discharge cycle at rated UCAP to verify MWh.; Solution Options2 B: initial test - CIR, annual/seasonal test qualification test similar to regulation
4A | rating methodology |  |  |  | Solution Options2 A: as other generation; Solution Options2 B: min instantaneous output for duration of test
5 | Metering requirements | low/medium | As Defined by Regulation market rules; Energy Market in Load Response Manual, LM Outlines in M11(Batteries), As outlined in M14D (storage) | As outlined in M14D | Solution Options2 A: Comply with rules in Manual 14D and 1; Solution Options2 B: Comply with rules in Manual 14D and 1
6 | How does a PJM Resource make itself available/Method of Availability to PJM | medium | Enter through queue process, Register as part of Markets Database, make themselves available trough eMarket- Traditional generators - daily must offer - DR - have to register prior to delivery year - if EO - 20 mins notice, self schedule | Enter through queue process, Register as part of Markets Database, make themselves available trough eMarket- Traditional generators - daily must offer - DR - have to register prior to delivery year - if EO - 20 mins notice, self schedule | Solution Options2 A: Must offer requirement applies to UCAP. Emergency procedures extend to full ICAP.; Solution Options2 B: energy market must offer obligations
7 | Offer parameters | high | N/A (Batteries), See Cap Market (Storage) | mins/max, startup, emergency min/max, price/cost based, cost curve Optimized Pumped Storage units only: 1) Beginning and End of Day Storage levels in MW. (INITIAL MW, FINAL MW) 2) GenMin and PumpMin values, which will be the minimum hourly pumping and generating MW (MIN PUMP MW, MIN GEN MW) 3) Pumping efficiency (PUMP FACTOR). 4) Maximum or minimum storage level constraints (MAX MW, MIN MW) Other parameters for regular resources as well: Start up/ shutdown costs | Solution Options2 A: status quo plus max run time and/or max energy and min charge time when using pumped hydro parameters, make obvious substitutions: pump/generate -> charge/discharge pumping efficiency -> cycle efficiency etc.; Solution Options2 B: status quo plus max run time and/or max energy and min charge time when using pumped hydro parameters, make obvious substitutions: pump/generate -> charge/discharge pumping efficiency -> cycle efficiency etc.
8 | Response and recovery | medium/high | Recovery=Min Down Time; Response=Notification time, max run time | Recovery=Min Down Time; Response=Notification time, max run time | Solution Options2 A: Notification time for RT energy may vary with charge state. Scheduling method in (1) must respect recharge times.; Solution Options2 B: Notification time for RT energy may vary with charge state. Scheduling method in (1) must respect recharge times.
9 | Capacity Value: How to determine UCAP | high | N/A (Batteries), See Cap Market (Storage) | - Discount ICAP based on outage rates, e.g., most gen - UCAP is fraction of ICAP, e.g., intermittent resources - Administratively determined, e.g., Energy Efficiency - Inferior product with limited clearing and price separation, e.g., sub-Annual DR. | Solution Options2 A: UCAP is the lesser of energy capacity divided by 3.3 or maximum output power. eFORd applied as for other generation. Treated as generation in RPM auctions; Solution Options2 B: Calculation based on load carrying capability at constant LOLE; Solution Options2 C: ICAP derated by forced outages; Solution Options2 D: actual output over series of peak hours (eg. Wind model); Solution Options2 E: average hourly output over req cont operation hourly req
10 | Applicability: what types of resources rules apply to | medium/high | N/A (Batteries), See Cap Market (Storage) | submit day ahead, schedule, blackstart level, never fully depleted | Solution Options2 A: Option A; Solution Options2 B: All interconnected storage devices not covered by current rules
11 | Scheduling method | low/medium |  |  | Solution Options2 A: Option A; Solution Options2 B: As specified in (1)
12 | Cost Based Offer Cap (Energy) | high |  |  | Solution Options2 A: Energy offer cap accounts for cost of purchased energy and cycle losses (e.g., net energy consumption)
12A | Cost Based Offer Cap (RPM)
13 | Emergency Procedures Obligations | medium |  |  | Solution Options2 A: During Min/MaxGen: 1. PJM may dispatch unit to charge/discharge at highest capable level, regardless of capacity obligation. 2. Unit not to discharge/charge except at PJM direction (following regulation signal counts as at PJM direction); Solution Options2 B: During Min/MaxGen: 1. PJM may dispatch unit to charge/discharge at highest capable level, regardless of capacity obligation. 2. Unit not to discharge/charge except at PJM direction (following regulation signal counts as at PJM direction)
14 | Performance Assessment | high | N/A (Batteries), See Cap Market (Storage) | - Seasonal verification test - EFORd and EFORp performance - DR compliance check - MMV for energy efficiency | Solution Options2 A: EFOR(x) counting only hours when scheduled for energy. Outages forgiven in hours following emergency energy dispatch.; Solution Options2 B: EFOR(x) counting only hours when scheduled for energy. Outages forgiven in hours following emergency energy dispatch.
15 | Settlements/Penalties | high |  |  | Solution Options2 A: As other generators, plus: 1. opportunity costs for transitions and "hold charge" hours included. 2. opportunity costs may be incurred during PJM directed charging as well as discharge. 3. make-whole payments if uneconomically dispatched by PJM (i.e., LMP while charging > efficiency * LMP while discharging); Solution Options2 B: As other generators, plus: 1. opportunity costs for transitions and "hold charge" hours included. 2. opportunity costs may be incurred during PJM directed charging as well as discharge. 3. make-whole payments if uneconomically dispatched by PJM (i.e., LMP while charging > efficiency * LMP while discharging)
16 | Immature resources/transition mechanisms for determining capacity value | medium/high |  | Class average values are blended with actual values on a monthly basis to produce EFORd values for future auctions | Solution Options2 A: Class average EFORd determined by review of storage currently in service; may be technology dependent.
Directions:
1Design Components - each is an "attribute" or "component" of any proposed solution. Consensus of the group should be sought on selection of a set of solution criteria.
2Solution Options - each is a solution alternative elicited from the stakeholder group that meet one of the specific solution criteria.
To complete the matrix:
1. Elicit from the stakeholder group a set of components (attributes) desired for any proposed solution. Enter a short label for each in the Design Components column.
2. If needed, enter a more detailed description of each criteria on the "Component Details" tab.
3. Using informal/non-binding voting, rate each component's priority in the final solution as "high/medium/low"
4. Elicit from the stakeholder group potential solution alternative(s) for each component. Enter a short label for each in the Solution Options columns.
5. If needed, enter a more detailed description of each potential solution option on the "Solution Details" tab.
6. Once the matrix is filled out, the group will attempt to select a single solution alternative (column) for each component (row) to form a solution "package".
Example: cells 1B, 2C, 3A, 4B, 5D could make up a solution package.
7. If consensus is achieved on a single package (Tier 1 decision-making method), this will be documented in a Consensus Proposal Report to the parent committee.
8. If not, the group will identify up to 3 possible solution packages in a comparative Proposal Alternatives Report to the parent committee (Tier 2 decision-making method).

## Proposal Matrix
Energy Storage Participation in RPM
PROPOSAL MATRIX
Packages
Number | Design Components1 | Priority (high/med/low) | Status Quo (Advanced Storage, Storage in PJM Today) | Status Quo (Resources in Capacity Market) | A (PJM Preferred) | B | C | D | E
1 | Must offer requirement in day ahead market | low/medium | N/A (Batteries), Required (Storage) | All resources in Capacity market have a Must Offer Req in Day ahead | All Generation resources with capacity commitment (including storage resources) Must offer in day ahead
2 | Minimum continuous electricity time capability | high | No Current Standard, Regulation ;market is hourly; cannot be out for XX mins, or else forfeit bid (Batteries), 10 hours (Storage) | 10 Hours | Sustained output for 10 hours continuous operation. Resource must produce its nominal capacity value for each hour of the 10 hour interval. Total storage capability of unit must support ability to provide its nominal capacity for 10 continuous hours. At full storage capability and probable time of PJM peak, resource must demonstrate empirically its ability to maintain the 10 hours capacity based on technical documentation. Value is capped at the CIR level
3 | Minimum continuous electricity production capability | low/medium | Continuous Capability for a certain period, 0.1 MW for existing resources (Batteries and Storage) | Continuous Capability for a certain period, 0.1 MW for existing resources | 0.1 MW for existing resources
4 | Test requirements | medium |  | - 1-2 hours based on resource type, Steam 2 hrs, Hydro 1 hr - Qualifying test - Seasonal test - Equivalent to duration | Perform annual test each summer (consistent with existing rules): Show that you can produce your nominal capacity value for 1 hour
4A | rating methodology |  |  |  | Based on min hourly output over 10 continuous hours. At full storage capability and probable time of PJM peak, resource must demonstrate empirically its ability to maintain the 10 hours capacity based on technical documentation
5 | Metering requirements | low/medium | As Defined by Regulation market rules; Energy Market in Load Response Manual, LM Outlines in M11(Batteries), As outlined in M14D (storage) | As outlined in M14D | Same metering requirement as all other generators, Units Co-located must have separate unit specific metering
6 | How does a PJM Resource make itself available/Method of Availability to PJM | medium | Enter through queue process, Register as part of Markets Database, make themselves available trough eMarket- Traditional generators - daily must offer - DR - have to register prior to delivery year - if EO - 20 mins notice, self schedule | Enter through queue process, Register as part of Markets Database, make themselves available trough eMarket- Traditional generators - daily must offer - DR - have to register prior to delivery year - if EO - 20 mins notice, self schedule | Alignment with the RPM current rules, available unless submitted an edart ticket
7 | Offer parameters | high | N/A (Batteries), See Cap Market (Storage) | mins/max, startup, emergency min/max, price/cost based, cost curve Optimized Pumped Storage units only: 1) Beginning and End of Day Storage levels in MW. (INITIAL MW, FINAL MW) 2) GenMin and PumpMin values, which will be the minimum hourly pumping and generating MW (MIN PUMP MW, MIN GEN MW) 3) Pumping efficiency (PUMP FACTOR). 4) Maximum or minimum storage level constraints (MAX MW, MIN MW) Other parameters for regular resources as well: Start up/ shutdown costs | status quo for existing generation
8 | Response and recovery | medium/high | Recovery=Min Down Time; Response=Notification time, max run time | Recovery=Min Down Time; Response=Notification time, max run time | status quo as for existing generation (default parameter to be determined)
9 | Capacity Value: How to determine UCAP | high | N/A (Batteries), See Cap Market (Storage) | - Discount ICAP based on outage rates, e.g., most gen - UCAP is fraction of ICAP, e.g., intermittent resources - Administratively determined, e.g., Energy Efficiency - Inferior product with limited clearing and price separation, e.g., sub-Annual DR. | ICAP determined by Design Component #2, UCAP calculated the same as all other units (some work required to collect Eford data for storage units, and to establish an advanced energy storage class average Eford)
10 | Applicability: what types of resources rules apply to | medium/high | N/A (Batteries), See Cap Market (Storage) | submit day ahead, schedule, blackstart level, never fully depleted | These proposed rules will apply to all Energy Storage Resources
11 | Scheduling method | low/medium |  |  | Should be bundled with Design Component #1
12 | Cost Based Offer Cap (Energy) | high |  |  | Similar to current units, but will need to be determined
12A | Cost Based Offer Cap (RPM) | high |  |  | Similar to current units, but will need to be determined by IMM
13 | Emergency Procedures Obligations | medium |  |  | Consistent with rules in M13 Section 6.4
14 | Performance Assessment | high | N/A (Batteries), See Cap Market (Storage) | - Seasonal verification test - EFORd and EFORp performance - DR compliance check - MMV for energy efficiency | Summer verification test; EFORd and EFORp performance
15 | Settlements/Penalties | high |  |  | Same as all other RPM Resources
16 | Immature resources/transition mechanisms for determining capacity value | medium/high |  | Class average values are blended with actual values on a monthly basis to produce EFORd values for future auctions | Status quo (how we test until class average is determined for any new technology type)
Instructions:
1. Copy over design component, priority, and status quo columns from options matrix
2. Complete individual packages in columns by selecting individual component options from the options matrix.