## Data
Committee-Topic | Slide Date | Q Source | Question | R Source | Response | Notes
PC | 2018-01-11 | Ryan Dolan, AMP | Can we share prelim analysis with all stakeholders, not just TO's? | PJM | That only happens with Reliability model. Everyone sees the model at the same time. Appreciate that there is a competitive sensitive.
PC | 2018-01-11 | Ryan Dolan, AMP | Can re-evaluation be moved to Phase 2? | PJM | Prob statements should be flexible. Should only incl Ph 1 in things that need to impact the upcoming proposal window.
PC | 2018-01-11 | Sharon Segnor, LS Power | PJM's stance is don't have legal authority or not willing to do review ROE. | PJM | We believe we have no power to enforce regulatory role.
PC | 2018-01-11 | Ed Tatum, AMP | Process question. OA changes. Need 2/3 approval at MRC, MC. What happens? | PJM | We will figure it out.
PC | 2018-01-11 | Ryan Dolan, AMP | Impact on analysis? | PJM | No change
PC | 2018-01-11 | Ryan Dolan, AMP | Non-firm long term included in the model. | PJM | Not included.
PC | 2018-01-11 | Ryan Dolan, AMP | Thinking about Linden, HVDC | PJM | Different topic. Not part of this discussion
PC | 2018-01-11 | Ryan Dolan, AMP | Is conversion from firm to non-firm a queue process? | PJM | No. non-firm is subordinate to firm. No change.
PC | 2018-01-11 | Ryan Dolan, AMP | What are the lowest impedance transformer on the system? | PJM | No idea.
PC | 2018-01-11 | Ryan Dolan, AMP | Lower impedance transformer react more. Change suggests lower quality test on more selective criteria. | PJM | Change is to better reflect reality.
PC | 2018-01-11 | Ryan Dolan, AMP | Studied how impacts gen entering queue? | PJM | Yes. One was in queue, was not.
PC | 2018-01-11 | Ryan Dolan, AMP | Impacts Trans Services & TRW? | PJM | Yes
PC | 2018-01-11 | Ryan Dolan, AMP | Was PJM incl P1 in Wnter analysis? | PJM | Yes. All contingencies. No change, correcting language.
PC | 2018-01-11 | Ryan Dolan, AMP | Exclude P3, P6 (N-1-1, ??)? | PJM | Yes.
PC | 2018-01-11 | Ryan Dolan, AMP | Severely constrain some gen. | PJM | Not changing
PC | 2018-01-11 | James Manning, NCEC | When rules applied? | PJM | If approved, will impact studies going forward.
PC | 2018-01-11 | James Manning, NCEC | Quanitfy impact? | PJM | yes.
PC | 2018-01-11 | Ryan Dolan, AMP | So we know one is overloaded. | PJM | Cannot assume that.
PC | 2018-01-11 | Ryan Dolan, AMP | Can review that project? | PJM | No. Will show some generic cases. Cannot share info no specific project.
PC | 2018-01-11 | Ryan Dolan, AMP | Slide 3. Number of changes between Trial 4 and Final | PJM | Should be none.
PC | 2018-01-11 | Ryan Dolan, AMP | Concern that TO's have access to mode ahead of other stakeholders. Release sooner. | PJM | Will consider.
PC | 2018-01-11 | James Manning, NCEC | slide 5. Just only study transformer? | PJM | No, focus is on transformer this year.
PC | 2018-01-11 | Ed Tatum, AMP | Appreciate discussion. Role of PJM. Need to level set in regional and local planning process. Well defined for regional (baseline). The meetings are not just bout PJM. They are for all stakeholders. Think the info is the minimum required for rational business decisions. For supplementals, need to go beyond "do no harm". 4 areas that should be considered. (Letter to Paul). Xxx, Transparency, Meeting formats, xxx. | PJM | will discuss at next PC. Continue to accept input.
PC | 2018-01-11 | Stephen Kelly, Brookfield Energy Marketing LP(?) | Take comments on redlines? How handle if entity buys firm rollover rights & �? | PJM | Yes. The goal is to retain parity. If there is no parity, add'l studies required.
PC | 2018-01-11 | Stephen Kelly, Brookfield Energy Marketing LP(?) | What about rollover rights? | PJM | Does not enter in. It just indicates the study to be performed.
PC | 2018-01-11 | Stephen Kelly, Brookfield Energy Marketing LP(?) | When submit studies, ID specific deficiencies for studies? | PJM | Yes.
PC | 2018-01-11 | Ed Tatum, AMP | First read? | PJM | Manual is not approved by PC. Under the MIC.
PC | 2018-01-11 | Ryan Dolan, AMP | If existing seam issue, and PJM does not address and it prevents incoming pseudo-ties, how handle? | PJM | Have seen that, if entity does not address, do not enter in.
PC | 2018-02-08 | Steve Lieberman, AMP | Don't see AMP agenda item on the agenda | PJM | Will be covered in Item 12. A lot of the information is duplicated. Discussion will be on going.
PC | 2018-02-08 | Carl Johnson, Customized Energy Solutions | Regarding OVEC. How handle with respect to integration date? Not complete yet. | PJM | Felt worth including not. If OVEC doesn't look like it will meet date, will witthold.
PC | 2018-02-08 | James Manning, NCEC | Regarding Light Load. Is this a change in procedure or a change in description? | PJM | Wording change only.
PC | 2018-02-08 | Ryan Dolan, AMP | Study of number of transformers impacted? Asked last time. Any info? Do we need to make adjustments. | PJM | Yes. Did analysis and little impact. Don't have info now. Will post and discuss offline.
PC | 2018-02-08 | Ryan Dolan, AMP | Request to withhold endorsement until stakeholders can evaluate. Went from 100+ to 5 transformers. | PJM | Agree on impact, but feel that the important stat is FGs that are impacted.
PC | 2018-02-08 | Ryan Dolan, AMP | Concern about the sensitivity to overload. | PJM | That is a lot of work. What info do you need to feel comfortable endorsing?
PC | 2018-02-08 | Ryan Dolan, AMP | Don't agree that it is a lot of work. What to see the impact on all transformers. Impacts gen trying attach to grid and how study reliability. | PJM | Can study and defer action.
PC | 2018-02-08 | Stephen Kelly, Brookfield Energy Marketing LP(?) | Process question. Posted on 2/5. Not 7 days, so it this a valid First Read. | PJM | It is 3 days for PC.
PC | 2018-02-08 | Stephen Kelly, Brookfield Energy Marketing LP(?) | Please verify with Dave Anders. | PJM | Confirm that PC is 3 days. Can talk through offline.
PC | 2018-02-08 | Stephen Kelly, Brookfield Energy Marketing LP(?) | How is this arise? Don't recall a charge statement. | PJM | Just language changes, not procedure changes.
PC | 2018-02-08 | Stephen Kelly, Brookfield Energy Marketing LP(?) | Change an "and" to and "or" why? Inconsistent. | PJM | Should be consistent. Will look.
PC | 2018-02-08 | Stephen Kelly, Brookfield Energy Marketing LP(?) | Sect 2xxx | PJM | For lower voltages, PJM cannot study. Will clarify language.
PC | 2018-02-08 | Stephen Kelly, Brookfield Energy Marketing LP(?) | Pg 6 of pdf. Don't like changes. Got a good system in place. Don't mess. | PJM | Acknowledge issue pending before FERC and should wait for FERC
PC | 2018-02-08 | Stephen Kelly, Brookfield Energy Marketing LP(?) | Under Summer Peak Analysis. "New Service Queue Request" should be "New Service Requests". Are the tests quoted correctly. | PJM | This is not meant to cover everythiing. This is just to say if application, apply these tests.
PC | 2018-02-08 | Stephen Kelly, Brookfield Energy Marketing LP(?) | "Storage type gen requests". Why only list 1 types? Why TO involved? | PJM | ID the most common types. Also depends on where in the system.
PC | 2018-02-08 | Stephen Kelly, Brookfield Energy Marketing LP(?) | Short Circ & . Concern of use of word "all". | PJM | Was not mention to eliminate engineering judgement.
PC | 2018-02-08 | James Manning, NCEC | Not redlines on section xx? | PJM | section was renumbered.
PC | 2018-02-08 | Ryan Dolan, AMP | DFAX cutoff limits for a contrib to overload. | PJM | Do not approve until overload is addressed. These are contributions to pre-existing overloads.
PC | 2018-02-08 | Ryan Dolan, AMP | Diff between RTEP process and interconnect process approval. Does PJM study all contributions. | PJM | There is a timeline impact on existing study and new services study. PJM needs to analyze who pays for what.
PC | 2018-02-08 | Ryan Dolan, AMP | Are all the old requests applied to new service request? Concern that Queue only considers firm transactions while non-firm is added to the RTEP analysis. Implies that ratepayers pay for overloads instead of interconnection customer. Concern that Cedar Grove overloads. | PJM | Can take offline.
PC | 2018-02-08 | Ryan Dolan, AMP | Prefer educational session for all stakeholders | PJM | Can do that. Suggest take Planning 201.
PC | 2018-02-08 | Ryan Dolan, AMP | Non-firm transactions are planned in RTEP and are creating overloads | PJM | Believe conflating non-frim withdraw with non-firm transactions.
PC | 2018-02-08 | Iker Chocarro Aguirrebengoa, E.ON | Can post Word so can redline? | PJM | Yes. Will do.
PC | 2018-02-08 | ITC(?) | Can you map out changes? | PJM | yes.
PC | 2018-02-08 | James Manning, NCEC | Please include redlines of the entire manual. Many changes and it's hard to follow. | PJM | ok
PC | 2018-02-08 | Dave Pratzon, GT Power Group | Seems like this is at odds with DER subcommittee. | PJM | Very possible. Once behind POI, different system. Need owners to work out the details.
PC | 2018-02-08 | John Brodbeck, EDP Renewables | Don't agree that 807 implies becoming a TO | PJM | to have the flexibility you want, you need to be a TO
PC | 2018-02-08 | John Horstman, Dayton |  | PJM | After 5 yrs of safe harbor, need to open to access.
PC | 2018-02-08 | Dave Pratzon, GT Power Group | Are these the default valuables unless can substantiate better performance? | PJM | Yes.
PC | 2018-02-08 | Barry Trayers, Citigroup Energy, Inc. | Do some additional differentiation? | PJM | Newer tech shows some improvements, but still not meaningful to do so.
PC | 2018-02-08 | Ed Tatum, AMP | in 1980, the remaining 10% were in June? | PJM | one was in Sept. but rest in June.
PC | 2018-02-08 | Iker Chocarro Aguirrebengoa, E.ON | Don't believe this are addressed previously. This was proposed 2 yrs ago. Why back now? What is the impact on the CIR? | PJM | Will apply going forward. May lessen reinforcements required.
PC | 2018-02-08 | ITC(?) | Need to elaborate on impacts of these changes. | PJM | ELCC studies have been completed. More detailed. Able to confirm assumption that media is a better estimate.
PC | 2018-02-08 | James Manning, NCEC | Yellow highlights are the language in question? | PJM | Yes.
PC | 2018-02-08 | Ed Tatum, AMP | Yellow changes are supported by PJM? | PJM | Yes. The last paragraph, however, is at issue with stakeholder
PC | 2018-02-08 | Bill Pazella, ODEC | Require projects present before in construction? | PJM | Request any impacts to system be shared with PJM.
PC | 2018-02-08 | Ryan Dolan, AMP | Recording of ques & answers from review. | PJM | Some of the items discussed are relative to TEAC & SRRTEP
PC | 2018-02-08 | Ed Tatum, AMP | Would like to follow up with understanding of M-14B. Want to work with stakeholders to address these issues. Would like to have the discussion more broadly that with AMP & PJM. | PJM | Not sure the best way to more forward. PJM has made some adjustments, AMP wants more.
PC | 2018-02-08 | Ed Tatum, AMP | AMP can offer a written list of questions and let PJM provide answers. PJM can provide details of how "Do no harm" analysis is done.
PC | 2018-02-08 | Barry Trayers, Citigroup Energy, Inc. | How soon updated? | PJM | within a few days of receiving deactiv notice.
PC | 2018-02-08 | Greg Paulson, Consumer Advocates | Resilience. Where is that conversation? FERC/DOE NOPR due. Consumer Advocates will file comments with PJM tomorrow. | PJM | MRC is addressing and has a request for comments. MRC has posted a proposed schedule.
PC | 2018-02-08 | Greg Paulson, Consumer Advocates | PJM has mentioned a number of resilience initiatives. Curious about progress and updates. | PJM | will bring back. Schedule has been full. Any impacts to planning process will come to PC.
PC | 2018-02-08 | Ryan Dolan, AMP | Is resilience quantifiable or qualitative? | PJM | It is an ongoing discussion.
PC | 2018-03-08 | Ryan Dolan, AMP | Is it typical for PJM to update manuals based on engineering judgement. | PJM | Yes. In fact most of the procedures are in fact based on engineering judgement. However, the judgement is validated by data.
PC | 2018-03-08 | Ryan Dolan, AMP | Why was 10% chosen initially? | PJM | Seemed reasonable at the time. Data has now indicated that 5% is more reasonable.
PC | 2018-03-08 | Ryan Dolan, AMP | Cutoffs of transformer vs lines? | PJM | ~5% on transformer and 10% on lines.
PC | 2018-03-08 | Ryan Dolan, AMP | Wonder about what data set was used? The 138kV values seem particularly small. | PJM | This is an ave. of the entire system.
PC | 2018-03-08 | Ryan Dolan, AMP | Gen Deliv analysis is performed in clusters. Wonder if a class av. Is appropriate? | PJM | Definitely will consider. However, we believe that it is providing a good model.
PC | 2018-03-08 | ?,Delphi | Trying to add more gens? | PJM | Yes.
PC | 2018-03-08 | Shadab Ali, PPL | When implimented? | PJM | Will apply to 2023 RTEP and going forward.
PC | 2018-03-08 | James Manning, NCEC | Can you please make this clear to MCR? Not clear at this presentation. | PJM | Yes.
PC | 2018-03-08 | Dave Pratzon, GT Power Group | For PTP service, participate but not in RPM. | PJM | Ok.
PC | 2018-03-08 | James Manning, NCEC | Presentation is clear. Wording is less so. | PJM
PC | 2018-03-08 | Ryan Dolan, AMP | Do MISO Gen Deliv test parallel PJM? | PJM | No. Getting closer.
PC | 2018-03-08 | Ryan Dolan, AMP | Has the difference been presented to stakeholders? | PJM | Yes. That is what the task force did last year. PJM is reaching out to impacted entities.
PC | 2018-03-08 | Ryan Dolan, AMP | Stability Question. If there is an existing stability.
PC | 2018-03-08 | Scarpa, Calpine | On slide 4, anything new? | PJM | No just adjusting language to reflect actual practice.
PC | 2018-03-08 | Ryan Dolan, AMP | Changes from prior read. | PJM | Mostly to align with tariff language.
PC | 2018-03-08 | Mike B, | Intermittent units pulls out wind and solar? | PJM | Yes, imtermittent now includes landfill gas, etc.
PC | 2018-03-08 | MB | What about units that have already locked in service? | PJM | Honor commitments. Not retroactive.
PC | 2018-03-08 | Ryan Dolan, AMP | Impact of supplementals on ME process. Don't see it mentioned. | PJM | Can talk about in Phase II. Don't need to explicitly state that.
PC | 2018-03-08 | Scarpa, Calpine | You are considering supplementals? | PJM | yes, we need to have good models, which include supplementals.
PC | 2018-03-08 | Ryan Dolan, AMP | Would be useful to mention supplementals. Would like a supplemental project modelled in ME not just modeled. | PJM | Don't need to mention it explicitly if everyone has consensus. If stakeholders feel that a statement is needed, it can be added.
PC | 2018-03-08 | Ryan Dolan, AMP | Ok to include a supplemental in a model. But want to consider if a supplemental will *impact* an issue. | Exelon | Think that economic impact of supplemental is beyond the scope of the task force.
PC | 2018-03-08 | Sharon Segnor, LS Power | Provided specific comments to ask include supplementals explicitly. | PJM | Believe it is included. Need a n educational phase then proceed from there.
PC | 2018-03-08 | Ryan Dolan, AMP | Does the generator need to be associated? | PJM | to avoid materiality, Merchant request is just a thermal analysis. Generators is still need to be evaluated individually.
PC | 2018-03-08 | Ryan Dolan, AMP | Partly related to M3. Is confidential info preventing transparent analysis of RTEP projects. | PJM | Looking into.
PC | 2018-03-08 | Ryan Dolan, AMP | Any economic analysis? | PJM | No.
PC | 2018-03-08 | James Manning, NCEC | No comments on TPL updates? | PJM | Not at this time.
PC | 2018-04-05 | ?? | Discussion on resilience? | PJM | Build on comments last year. Develop ideas and layout.
PC | 2018-04-05 | Adrien Ford, ODEC | What are "documents"? Not regs, not manuals. Want to understand the context | DOM | Predates NERC standards. Many util. still reference this doc. Foresee this document going away. It is guidance. No basis for "enforcement"
PC | 2018-04-05 | Carl Johnson, Customized Energy Solutions | Not read all fillings. Does geographic break out make sense? | PJM | That makes sense.
PC | 2018-04-05 | Ryan Dolan, AMP | Should PJM wait while FERC proceeding is in play? | PJM | Not suggesting a delay. Starting discussion.
PC | 2018-04-05 | Ryan Dolan, AMP | Alignment of supplementals with RTEP cycles. Is that in scope? | PJM | Can discuss.
PC | 2018-04-05 | PJM Indus Coalition | Endurce. Share concern of understanding details of ratings. Trust but verify. | PJM | Historically, PJM develops info ahead of NERC standards.
PC | 2018-04-05 | Carl Johnson, Customized Energy Solutions | Process? Problem statement? | PJM | No plan to issue problem statement. Will continue discussion with AMP and interested parties.
PC | 2018-05-03 | Steve Lieberman, AMP | Don't understand the agenda. Don't understand the 3 informational update sections. | PJM
PC | 2018-05-03 | James Manning, NCEC | QueuePoint is the consumer info connection. Voted on other changes. See some notes stricken. Could be useful. | PJM
PC | 2018-05-03 | James Manning, NCEC | Basis for changing from 4 to 8 months. | DOM | NERC does not spec maint. Intervals. One stakeholder asked for a change to align with their practices.
PC | 2018-05-03 | Adrien Ford, ODEC | Observation, concerned about including forced outages in forecast, also concerned about using actual data. Also understand the polar vortex 1 taken out and using polar vortex 2. | PJM | Will roll in additional data. Really no 2nd option. Historical data is the best we have.
PC | 2018-05-03 | Kameron, PSEG | Impact on IRM? | PJM | IRM suggests no increase.
PC | 2018-05-03 | Tom Shields, IBERDROLA RENEWABLES(?) | No following closely. Summer have the same issues? | PJM | Looked at summer. Don't see the same shift in data.
PC | 2018-05-03 | Jim Wilson, Consumer Advocates | Echo historical concern. Letter at RAAS, consider reserve requirement study in resource adequacyconsideration. | PJM | Will wrap into white paper.
PC | 2018-05-03 | Steve Lieberman, AMP | Date of next RAAS? | PJM | Was not set at the time slides were created. Will be May 31.
PC | 2018-05-03 | Steve Lieberman, AMP | PJM proposal has changed from failed version. Please highlight changes. LS Power as well. | PJM | Next item is to do just that.
PC | 2018-05-03 | Ryan Dolan, AMP | What considerations have changed from prior proposal? | PJM | I will address.
PC | 2018-05-03 | James Manning, NCEC | What will be in the end-of-rtep summary table? | PJM | on screen. Details will still be posted as well. Will indicate what works and doesn't. Will quantify what can be quantified. Try to qualify those that cannot.
PC | 2018-05-03 | Greg Paulson, Consumer Advocates | Would like to see more than just construction cost. Happy that revenue is considered. Might want PJM to go further. How does this differ from the status quo? | PJM | Yes, we do consider all proposals. But need to make cost caps more prominent.
PC | 2018-05-03 | Greg Paulson, Consumer Advocates | How handle cost cap with existing process. All else being equal | PJM | Never really happens. And it really depends on the revenue requirements. Some are difficult to quantify.
PC | 2018-05-03 | Adrien Ford, ODEC | Support cost cap on construction costs only. Should not include ROE or other
PC | 2018-05-03 | Brian Wilkie, ConEd | Enforceability by PJM at FERC & courts. | PJM | rates are enforced by FERC. Is in the DEA. FERC has been enforcing. Notice of exceeding cost cap must be sent to PJM, who in turn notifies stakeholders & FERC.
PC | 2018-05-03 | Tanya Wicks, Duquesne | Concern about timeliness of review? How address? | PJM | Violations have been going down, so workload is lower. So, PJM has been able to manage workload. Concern that if these trends change, would PJM be able to keep up?
PC | 2018-05-03 | Greg Paulson, Consumer Advocates | Concern about enforceability. Courts have repeatedly ruled that PJM does not have that authority. | PJM | We believe we are following the tariff. Will take it to Legal.
PC | 2018-05-03 | Stephen Kelly, Brookfield Energy Marketing LP(?) | Slide 9 & 10. If Developer submits cost containment bid, why is PJM concerned about cost estimate? | PJM | Need to consider that the cost estimates are reasonable and good utility practices are included. Don't want to setup up for failure.
PC | 2018-05-03 | Stephen Kelly, Brookfield Energy Marketing LP(?) | Will there be a discussion with developer, not just outright reject? | PJM | That is the process today. And shared with
PC | 2018-05-03 | John Bing | Question about Excel template. Items about incumbent work. Are developers expected to collect that info? | PJM | No. PJM will follow up.
PC | 2018-05-03 | Stephen Kelly, Brookfield Energy Marketing LP(?) | PJM has not seen the trivial proposals. Goes to pre-qual process. Emphasize the dialogue with developer regarding costs and assumptions. | PJM | Agree. That is today's process. Will continue going forward.
SRRTEP-MA | 2017-12-19 | Ryan Dolan, AMP | Flowgate detail? Can't find it. | PJM | Posted. Will help you find it.
SRRTEP-MA | 2017-12-19 | Ryan Dolan, AMP | What changed. | DPL | Update from wholesale customer.
SRRTEP-MA | 2017-12-19 | Ryan Dolan, AMP | Contingencies? | DPL | Loss of Cool Springs, or Indian River -Robinson
SRRTEP-MA | 2017-12-19 | Ryan Dolan, AMP | On list of market monitored elements? | PJM | yes.
SRRTEP-MA | 2017-12-19 | Bill Pazella, ODEC | First or second read of this project? | PSEG | First
SRRTEP-MA | 2017-12-19 | Bill Pazella, ODEC | When come back with second read? | PSEG | Hope to be back in Jan, but will get approval from City before return.
SRRTEP-MA | 2017-12-19 | Ryan Dolan, AMP | Why no 138kV to Koller Rd. | PSEG | No space and additional line cost.
SRRTEP-MA | 2017-12-19 | Ryan Dolan, AMP | Why convert Koller Rd. from 138 to 69kV? | PSEG | no space. More cost effect.
SRRTEP-MA | 2017-12-19 | Ryan Dolan, AMP | How can add 2 lines but can't add 138kV? | PSEG | 69kV takes less space, all overhead.
SRRTEP-MA | 2017-12-19 | Ryan Dolan, AMP | Passaic-Patterson 69kV line previously presented? | PSEG | Yes.
SRRTEP-MA | 2017-12-19 | Ryan Dolan, AMP | How to rebuild and provide support? | PSEG | part of normal process.
SRRTEP-MA | 2017-12-19 | Joe Delosa, DE Commission Staff | Why baseline? | PJM | Due to FERC 715 criteria.
SRRTEP-MA | 2017-12-19 | Ryan Dolan, AMP | 230-26, 230-13kV conversion. Add'l transformation? | PSEG | No
SRRTEP-MA | 2017-12-19 | Ryan Dolan, AMP | How many transformers? | PSEG | 2 230-26 and 4 230-13
SRRTEP-MA | 2017-12-19 | Ryan Dolan, AMP | Does 26kV serve load? | PSEG | Mostly other stations. Some large customers.
SRRTEP-MA | 2017-12-19 | Ryan Dolan, AMP | Model 26kV? PJM has? | PSEG | Yes. No.
SRRTEP-MA | 2017-12-19 | Ryan Dolan, AMP | is 26kV coordinated with system? | PSEG | Yes.
SRRTEP-MA | 2017-12-19 | Ryan Dolan, AMP | Power factor of N.Bridge load? | PSEG | About 96%
SRRTEP-MA | 2017-12-19 | Ryan Dolan, AMP | Why was not a stat com, cap bank considered? (Statcom is dynamic) | PSEG | Studied. Did not resolve problem.
SRRTEP-MA | 2017-12-19 | Ryan Dolan, AMP | Building lines to address a reactive issue. Wouldn't a reactor work. | PSEG | Add'l reactive was reviewed. Not helpful.
SRRTEP-MA | 2017-12-19 | Ryan Dolan, AMP | Was power factor correction considered? | PSEG | Customer load.
SRRTEP-MA | 2017-12-19 | Ryan Dolan, AMP | Power factor | PSEG | Keep PF to 96%, saturate area with cap banks. Most are pole mounted. Many small cap banks. Static but act as dynamic.
SRRTEP-MA | 2017-12-19 | Ryan Dolan, AMP | Allow cap banks to switch between 1st and 2nd conting? | PSEG | Yes.
SRRTEP-MA | 2017-12-19 | Ryan Dolan, AMP | Allow cap banks switching after 2nd conting? | PSEG | No.
SRRTEP-MA | 2017-12-19 | Ryan Dolan, AMP | Allow manual switch rebefore 2nd conting. | PSEG | Follow NERC criteria.
SRRTEP-MA | 2017-12-19 | Ryan Dolan, AMP | Any limitations on adjustments? | PSEG | Not.
SRRTEP-MA | 2017-12-19 | Ryan Dolan, AMP | Would PSEG consider a switching solution? | PSEG | Limiting discussion to Bridgeport. Comfortable with proposed solution.
SRRTEP-MA | 2017-12-19 | Ryan Dolan, AMP | Not willing to consider alternatives? | PJM | PSEG has heard the alternatives and they
SRRTEP-MA | 2017-12-19 | Ryan Dolan, AMP | Show cause | PSEG | this issue is before FERC. FERC will judge interpretation. Inappropriate to discuss here.
SRRTEP-MA | 2017-12-19 | Ryan Dolan, AMP | Present alternatives. Will it be considered? | PJM | Yes.
SRRTEP-MA | 2017-12-19 | Ryan Dolan, AMP | Will implement if meets criteria and is cheaper? | PJM | No, can't guarantee.
SRRTEP-MA | 2017-12-19 | PJM Industrial Coalition | Timing for advancing projects to approval. | PJM | Baseline projects go forward to Board in Februrary.
SRRTEP-MA | 2018-01-26 | Ryan Dolan, AMP | Why not back into hazelwood. | BGE | Same ducts can't be reused. Limited connection points. This provides greater flexiblity.
SRRTEP-MA | 2018-01-26 | Ryan Dolan, AMP | any load served from hazelwood? | BGE | There is but not on this side of the station.
SRRTEP-MA | 2018-01-26 | Ryan Dolan, AMP | Retain tap at Haselwood? | BGE | CB's are downstream of tap. No impact by retiring CB.
SRRTEP-MA | 2018-01-26 | Ryan Dolan, AMP | Expect a lot of work to re-config station to breaker & half. Why not install single circ? Why not just make this one project, instead of two? | BGE | Distrib station rebuild need drives some decision. Projects have different drivers. Adds reliability and flexibility.
SRRTEP-MA | 2018-01-26 | Ryan Dolan, AMP | any CB at Summerfield? | BGE | No. T-tap, no CB. Texa s not radial. Map may be incorrect.
SRRTEP-MA | 2018-01-26 | Ryan Dolan, AMP | Why not go to Cold Springs? | BGE | This is the best route. We are also looking at access to Cold Springs.
SRRTEP-MA | 2018-01-26 | Ryan Dolan, AMP | Cost is total on all CB or for each? | BGE | For all CBs.
SRRTEP-MA | 2018-01-26 | Ryan Dolan, AMP | Any particular (class) issues with CBs? | BGE | Oil in general. All are problematic. All with the condition. All at least 30 yrs, many are 40 yrs.
SRRTEP-MA | 2018-01-26 | Ryan Dolan, AMP | Are the CBs fully depreciated? Fault operations? | BGE | No idea about financial, Can get ops. NE
SRRTEP-MA | 2018-01-26 | Ryan Dolan, AMP | What is fault duty? | BGE | Will have on next review.
SRRTEP-MA | 2018-03-23 | Ryan Dolan, AMP | Shift load. How much is being shifted? | AEP | 15MVA
SRRTEP-MA | 2018-03-23 | Ryan Dolan, AMP | CBs at Sub? CBs separate the transformers | AEP | Yes. Line bus.
SRRTEP-MA | 2018-03-23 | Ryan Dolan, AMP | Both transformers overload. Adding 3rd resolves overload? | AEP | Yes. Yes.
SRRTEP-MA | 2018-03-23 | Ryan Dolan, AMP | Final bus config? | AEP | 7 breaker ring bus
SRRTEP-MA | 2018-03-23 | Ryan Dolan, AMP | Trans upgrade justified by Dist need? | AEP | Yes. This is the best alternative. Also brings station up to standard.
SRRTEP-MA | 2018-03-23 | Ryan Dolan, AMP | Loading and age? Larger than 41 MVA? Why not replace with transformers and keep distrib. | AEP | Don't have age. Yes. Considered transformer upgrade. T upgrade is most cost effective. Best investment.
SRRTEP-MA | 2018-03-23 | Ryan Dolan, AMP | Est Cost | AEP | ~$6M
SRRTEP-MA | 2018-03-23 | Ryan Dolan, AMP | Age. Current conductor. Cu is limit? What is the limit. | AEP | About 65 yrs old. 75 ACSR, 2/0 Cu. Yes. 65MVA (N&E)
SRRTEP-MA | 2018-03-23 | Ryan Dolan, AMP | Perform based on # outages? | AEP | based on condition. Condition asset presented
SRRTEP-MA | 2018-03-23 | Ryan Dolan, AMP | No performance issues? | AEP | One perm outage. Static wire failure.
SRRTEP-MA | 2018-03-23 | Ryan Dolan, AMP | Last inspections? | AEP | done on a 5 yr cycle. So not more that 5 yrs.
SRRTEP-MA | 2018-03-23 | Ryan Dolan, AMP | Make model available to public? | AEP | No. Use as a tool in making decision.
SRRTEP-MA | 2018-03-23 | Ryan Dolan, AMP | As address 1st quartile, just do them? | AEP | Updated annually. Focus on top quartile.
SRRTEP-MA | 2018-03-23 | Ryan Dolan, AMP | What happens if all the top quartile addressed? Would you rebuild a line that is only 10 years old? | AEP | It is a tool that helps ID need. It is not a bright line test. Use engineering judgement.
SRRTEP-MA | 2018-03-23 | Ryan Dolan, AMP | Cost & conductor? | AEP | $11M, 795 ACSR
SRRTEP-MA | 2018-03-23 | Ryan Dolan, AMP | Load at Cape May? | AEP | ~40MVA
SRRTEP-MA | 2018-03-23 | Ryan Dolan, AMP | Any other load? Why such large conductor? Justified? | AEP
SRRTEP-MA | 2018-03-23 | Joe Delosa, DE Commission Staff | What doc is are | AEP | Is posted on TRPSTF committee
SRRTEP-MA | 2018-03-23 | Ryan Dolan, AMP | Cost? | AEP | ~$11M
SRRTEP-MA | 2018-03-23 | Ryan Dolan, AMP | Other leg of radial system? | AEP | yes.
SRRTEP-MA | 2018-03-23 | Ryan Dolan, AMP | Was a D/C considered? | AEP | No. Because it is the end of the line, diverse path preferred.
SRRTEP-MA | 2018-03-23 | Ryan Dolan, AMP | D feeders? | AEP | Don't have. Do we need this info?
SRRTEP-MA | 2018-03-23 | Ryan Dolan, AMP | More than one D feeder? | AEP | Yes.
SRRTEP-MA | 2018-03-23 | Ryan Dolan, AMP | Age? | AEP | ~65 yrs.
SRRTEP-MA | 2018-03-23 | Ryan Dolan, AMP | Post additional justification? Post pictures? | AEP | No. Aerial inspect. Last done 2016. No pictures.
SRRTEP-MA | 2018-03-23 | Bill Pazella, ODEC | N-1 projected to reach E limit. Load increase? | AEP | Identified by distrib.
SRRTEP-MA | 2018-03-23 | ODEC | Plan to add 23kV lines? | AEP | Upgrade to 69kV. No impact ot distrib voltages.
SRRTEP-MA | 2018-03-23 | ODEC | Consider adding 23kV lines? | AEP | Grid Resiliency to barrier island. $70M, Order of mag higher. 40 MVA load. Barrier island. Use UG.
SRRTEP-MA | 2018-03-23 | Ryan Dolan, AMP | Currently UG? | AEP | Yes portions. UG ducts, bridge ducts, some aerial.
SRRTEP-MA | 2018-03-23 | Ryan Dolan, AMP | Age? | AEP | Don't have.
SRRTEP-MA | 2018-03-23 | Ryan Dolan, AMP | Would a 3rd line be more resilient? | AEP | Yes. But trying to eliminate 23kV on system.
SRRTEP-MA | 2018-03-23 | Ryan Dolan, AMP | Costs are going to entire zone. | AEP | This is the most appropriate solution. Filed to NJ PUC as a grid resilience project. Accepted.
SRRTEP-MA | 2018-03-23 | Bill Pazella, ODEC | Monopole with 6 conductors? | BGE | rebuilding with 3 conductors.
SRRTEP-MA | 2018-03-23 | Ryan Dolan, AMP | What causes outages? | BGE | Avian, splice failure, weather.
SRRTEP-MA | 2018-03-23 | Ryan Dolan, AMP | Upgraded voltage? Is this good util practice? | BGE | was 66kV.
SRRTEP-MA | 2018-03-23 | Ryan Dolan, AMP | Upgrade insulators? | BGE | Since clearance issues.
SRRTEP-MA | 2018-03-23 | Ryan Dolan, AMP | Outages on BGE or PPL side? | BGE | Probably PPL.
SRRTEP-MA | 2018-03-23 | Ryan Dolan, AMP | What type of outages by BGE? | BGE | Not have info.
SRRTEP-MA | 2018-03-23 | Ryan Dolan, AMP | Cost? Will bring back if cost increases? | BGE | ~$4M for pref. Will do.
SRRTEP-MA | 2018-03-23 | Ruth Price, DE Consumer Advocate | Cost? | DPL | ~$2M
SRRTEP-MA | 2018-03-23 | Bill Pazella, ODEC | Types of outages? How do CB help? | DPL | No high side CB. Several outages.
SRRTEP-MA | 2018-03-23 | Bill Pazella, ODEC | How many feeds? | DPL | Looped circuit.
SRRTEP-MA | 2018-03-23 | Ruth Price, DE Consumer Advocate | 69kV or upgrade | DPL | now 69kV. 40MVA, About the same
SRRTEP-MA | 2018-03-23 | Ryan Dolan, AMP | Your ROW? | DPL | 2 sep circ, 2 sep ROW
SRRTEP-MA | 2018-03-23 | Ryan Dolan, AMP | Why 3 CB? | DPL | One CB each line, CB between xfrmrs
SRRTEP-MA | 2018-03-23 | Ruth Price, DE Consumer Advocate | Written std. | DPL | Yes. Included in published . Typ. Would use ring bus, but no space for that.
SRRTEP-MA | 2018-03-23 | Ruth Price, DE Consumer Advocate | Outages? | DPL | 5 permanent, tornado.
SRRTEP-MA | 2018-03-23 | Joe Delosa, DE Commission Staff | If tornado hits new line, how long to restore? Would a the new line be more resilient? | DPL | Wood pole damage. Could happen again. Current config, station sees both feeds as a single line. Can isolate fault.
SRRTEP-MA | 2018-03-23 | Ruth Price, DE Consumer Advocate | Creating redundancy? | DPL
SRRTEP-MA | 2018-03-23 | Ryan Dolan, AMP | What circ where impacted by tornado?
SRRTEP-MA | 2018-03-23 | Ryan Dolan, AMP | Did you consider MOABs? | DPL | No. CBs are preferred.
SRRTEP-MA | 2018-03-23 | Ruth Price, DE Consumer Advocate | Cost for #10, 11, 12 | DPL | ~2.2M, 1.8M, $35M
SRRTEP-MA | 2018-03-23 | Ruth Price, DE Consumer Advocate | Current line? Outages? Sustained outage define? | DPL | 69kV. Tree, insul, consumer faults(3 sustained, 10 T) Believe 1 - 5 min.
SRRTEP-MA | 2018-03-23 | Ruth Price, DE Consumer Advocate | Age? | DPL | 50 - 60 yrs. One of the worst performing lines in system.
SRRTEP-MA | 2018-03-23 | Ryan Dolan, AMP | How op Chestertown term? | DPL | Ring bus but N.O.
SRRTEP-MA | 2018-03-23 | Ryan Dolan, AMP | Why N.O.? Would N.C. improve reliability? | DPL | Relay issues at Chestertown. Working to resolve as well. Should see soon.
SRRTEP-MA | 2018-03-23 | Ryan Dolan, AMP | How many "danger trees"? Condition of ROW? | DPL | Don't have that info. Can check with veg mgmt.
SRRTEP-MA | 2018-03-23 | Ryan Dolan, AMP | How decide best location for CB? Did you coord with REA coop? Can they install series CB? | DPL | CB need to be owned by DPL.
SRRTEP-MA | 2018-03-23 | Ryan Dolan, AMP | How ensure coop has a comparable protection. | PJM/DPL | Can we take offline?/ Talk with Choptank, ODEC, CEC regularly. No concerned raised.
SRRTEP-MA | 2018-03-23 | Ryan Dolan, AMP | No issues with reliability? | DPL | Not that we aware of.
SRRTEP-MA | 2018-03-23 | Bill Pazella, ODEC | Can expect project to rebuild southern loop of circuit? | DPL | No. But can expect project to upgrade Chestertown.
SRRTEP-MA | 2018-03-23 | Ryan Dolan, AMP | Volt threshold for FERC 715. Magnitude and deviation criteria? | DPL | +/- 5%. Don't have in front of us. FERC 715 is publicly filed.
SRRTEP-MA | 2018-03-23 | Bill Pazella, ODEC | conductor size? | DPL | exist- 336 ACSR ;new- 954 ACSR?
SRRTEP-MA | 2018-03-23 | Bill Pazella, ODEC | Compare with lines adjacent? | DPL | 954 north, 636 ACSR south
SRRTEP-MA | 2018-03-23 | Bill Pazella, ODEC | Will upgrade south, Load needs it? | DPL | No, load does not require.
SRRTEP-MA | 2018-03-23 | Bill Pazella, ODEC | Taylor Tap. Any changes? | DPL | Tap remains.
SRRTEP-MA | 2018-03-23 | Ruth Price, DE Consumer Advocate | Cost? Aerial inspect? | DPL | $7.2M. Yes.
SRRTEP-MA | 2018-03-23 | Ryan Dolan, AMP | Steel pole less O&M thanwood? | DPL | Yes.
SRRTEP-MA | 2018-03-23 | Ruth Price, DE Consumer Advocate | What is loading on line? | DPL | Don't have.
SRRTEP-MA | 2018-03-23 | Ryan Dolan, AMP | Can operators close into another path to support an alternate path. | DPL | This is an deteriorating condition. How does an alternate path address the issue?
SRRTEP-MA | 2018-03-23 | Exelon | Getting into distribution modeling? | Ryan Dolan, AMP | No we are not.
SRRTEP-MA | 2018-03-23 | Bill Pazella, ODEC | Existing conductor, prop. | DPL | 954 ACSR new. 136MVA E, 636 ACSR
SRRTEP-MA | 2018-03-23 | Ruth Price, DE Consumer Advocate | Cost? | DPL
SRRTEP-MA | 2018-03-23 | Joe Delosa, DE Commission Staff | Missed ex
SRRTEP-MA | 2018-03-23 | Ryan Dolan, AMP | Peak 60MVA? | DPL | Yes.
SRRTEP-MA | 2018-03-23 | Ryan Dolan, AMP | Alternatives other than rebuilding a line? | DPL | Consider a new line.
SRRTEP-MA | 2018-03-23 | Ryan Dolan, AMP | Could the line be retired? | DPL | Removing line, overloads other lines. Did not pursue further.
SRRTEP-MA | 2018-03-23 | Joe Delosa, DE Commission Staff | What is the load forecast in the area? Why need such a high load capacity. | DPL | This is the std. conductor size.
SRRTEP-MA | 2018-03-23 | Ruth Price, DE Consumer Advocate | Can visually coaborate ? | DPL | Yes.
SRRTEP-MA | 2018-03-23 | Ryan Dolan, AMP | 754 ACSR. Design for 120 mph. 1.5 ice, angle 90. Blindly apply standards, is that optimal? Can you ensure this is the cheapest cost? | DPL/Exelon | yes. This is the current standard. / Stepping into a prudency discussion. Leads into supply strategy.
SRRTEP-MA | 2018-03-23 | Ruth Price, DE Consumer Advocate | Load rating? | DPL | Peak load seen, 60MVA. There are also contingency loads which could drive higher.
SRRTEP-MA | 2018-03-23 | Ruth Price, DE Consumer Advocate | Outages related to line? | DPL | No sustained outages.
SRRTEP-MA | 2018-03-23 | Ryan Dolan, AMP | Impact of performance risk? | DPL | No specific lose of load. But a networked line, increase reliability.
SRRTEP-MA | 2018-03-23 | Ryan Dolan, AMP | Run N-1-1 analysis on 69kV. | DPL | Look at but not part of FERC 715 criteria.
SRRTEP-MA | 2018-03-23 | Ryan Dolan, AMP | Did you look at bringing ing Silver Side Rd -Edgemoor into sub? | DPL | No.
SRRTEP-MA | 2018-03-23 | Ryan Dolan, AMP | Sizes, ratings, etc. | DPL | 336 ACSR old, 954 ACSR new
SRRTEP-MA | 2018-03-23 | Ryan Dolan, AMP | ENM-Todd. Rating, condition? | DPL | Don't have that. 954 ACSR in place.
SRRTEP-MA | 2018-03-23 | ? | Cost? | DPL | $22M
SRRTEP-MA | 2018-03-23 | Bill Pazella, ODEC | Loop to Cambridge and back through w. Cambrdige? | DPL | Existing lopp, no config changes.
SRRTEP-MA | 2018-03-23 | Bill Pazella, ODEC | 11.5 mi. How long is slide 14. | DPL | ~$1.5mi.
SRRTEP-MA | 2018-03-23 | Joe Delosa, DE Commission Staff | Loading. | DPL | 40MVA
SRRTEP-MA | 2018-03-23 | Joe Delosa, DE Commission Staff | Same concerns about condutor size.
SRRTEP-MA | 2018-03-23 | Ryan Dolan, AMP | What is not protected? | MetEd | transformer are directly connected to the bus. transformer fault takes out the entire bus. Station laid out for dbl bkr. Easier / cheaper to continue build out. By replacing 2 & 5 elim 230kV relocating.
SRRTEP-MA | 2018-03-23 | Ryan Dolan, AMP | <trying to redesign the station | MetEd | makes no sense. Not going to do use 9 CB to protect a transformer. also addresses PCLRs on #5. Available on PJM database.
SRRTEP-MA | 2018-03-23 | Ryan Dolan, AMP | CB on line, is it a T asset? | MetEd | Yes.
SRRTEP-MA | 2018-03-23 | Ryan Dolan, AMP | So can connect to a bus and get revenue? | ME | Not any more.
SRRTEP-MA | 2018-03-23 | Ryan Dolan, AMP | Why are customers paying? | FE | This is legacy system. Have seen loss on this circuit. It improves service to customers.
SRRTEP-MA | 2018-03-23 | Ryan Dolan, AMP | Do you do this for all legacy situations? | FE | This is a case-by-case analysis. It makes sense here.
SRRTEP-MA | 2018-03-23 | Ryan Dolan, AMP | Gen is not a network path | FE | Yes, it is a network path.
SRRTEP-MA | 2018-03-23 | Ryan Dolan, AMP | Does that make the gen lead line a trans asset? | FE | It does not enter into it. It is a reliability upgrade to improve
SRRTEP-MA | 2018-03-23 | Ryan Dolan, AMP | What about split bus and add CB there? | MetEd | No.
SRRTEP-MA | 2018-03-23 | Ryan Dolan, AMP | Who owes gen? | FE | No idea, not relevant.
SRRTEP-MA | 2018-03-23 | Ryan Dolan, AMP | Standard for circ switchers. | PennElec | do not allow Circ Switch at this voltage.
SRRTEP-MA | 2018-03-23 | Ryan Dolan, AMP | 3 winding? | PennElec | Don't recall. Typically auto-transformer.
SRRTEP-MA | 2018-03-23 | Ryan Dolan, AMP | No Distrib work? | PennElec | No.
SRRTEP-MA | 2018-03-23 | Bill Pazella, ODEC | Add ring bus on 138 or 115 side? | PennElec | 115kV side
SRRTEP-MA | 2018-03-23 | Bill Pazella, ODEC | 1 transformer still sufficient? | PennElec | yes.
SRRTEP-MA | 2018-03-23 | Ryan Dolan, AMP | Change 138 to 115? | PennElec | Not going to change south stations to 115, so talking about building a new station. Makes no sense.
SRRTEP-MA | 2018-03-23 | Ryan Dolan, AMP | Aaron, wouldn't that be an operational baseline project? | PJM | Need to review. Not sure.
SRRTEP-MA | 2018-03-23 | Ryan Dolan, AMP | Ratings? | PennElec | 115 lines are limited by conductor. 138 increases, limiting element is conductor. transformer is rated higher than line.
SRRTEP-MA | 2018-03-23 | Bill Pazella, ODEC | Is there a problem at station? | PennElec | transformer tied to straight bus with switch. 13 outages in 5 yrs related to this.
SRRTEP-MA | 2018-03-23 | Bill Pazella, ODEC | written standard? | PennElec | Internal guidance, not published.
SRRTEP-MA | 2018-03-23 | Ryan Dolan, AMP | If 35 outages, how many are lines or stations. | FE | Caution about discussing CEII info in an open forum. Happy to discuss off line.
SRRTEP-MA | 2018-03-23 | Ryan Dolan, AMP | Can't talk about any station projects? | PJM | Would not say that. Can ask generally and take detailed dicussion off line.
SRRTEP-MA | 2018-03-23 | Ryan Dolan, AMP | See lots of CB. How many line faults caused distrib outage. | PennElec | Don't have the info. Not a driver for the project.
SRRTEP-MA | 2018-03-23 | Ryan Dolan, AMP | How feed transformer after? | PennElec | out of the ring.
SRRTEP-MA | 2018-03-23 | Ryan Dolan, AMP | <questions about what defines a bus outage | FE | Ryan, Craig has answered your question 3 times.
SRRTEP-MA | 2018-03-23 | Ryan Dolan, AMP | Potential overload in last RTEP, but removed. Might that eliminate the existing project? | PJM | Looking at it. Don't think will elim.
SRRTEP-MA | 2018-03-23 | Ryan Dolan, AMP | More detail on events that cause | PJM/PSEG | Related to UG service and restoration time./ Line and transformer
SRRTEP-MA | 2018-03-23 | Ryan Dolan, AMP | 9% overload with or without load growth? | PSEG | Existing.
SRRTEP-MA | 2018-03-23 | Ryan Dolan, AMP | Cap bank on what voltage? | PSEG | 69kV
SRRTEP-MA | 2018-03-23 | Ryan Dolan, AMP | Gen Deliv analayis? | PJM | had not completed analysis?
SRRTEP-MA | 2018-03-23 | Ryan Dolan, AMP | What config will analyze? | PJM | start with low cost.
SRRTEP-MA | 2018-03-23 | Alex Stern, PSEG | Get through all the slides? | PJM | That's the goal.
SRRTEP-MA | 2018-03-23 | Ryan Dolan, AMP | Would this project elim the trenton switch proj?
SRRTEP-MA | 2018-03-23 | Ryan Dolan, AMP | Will PJM look at both solutions to see if one addresses the other. | PJM | Will look at them. Don't see the opportunity.
SRRTEP-MA | 2018-03-23 | Bill Pazella, ODEC | Will this be a radial line? | UGI | D/C in and out. Network config.
SRRTEP-MA | 2018-03-23 | Bill Pazella, ODEC | Need additional CB at origination? | UGI | No. Not a tap per se. break line.
SRRTEP-MA | 2018-03-23 | Ryan Dolan, AMP | Is there a high side CB? | UGI | there is a high side cb. No network interupt due to transformer.
SRRTEP-MA | 2018-03-23 | Ryan Dolan, AMP | Consider ring bus? | UGI | Believe is over kill.
SRRTEP-MA | 2018-03-23 | Ryan Dolan, AMP | Consider CB failure. | UGI | Can look at.
SRRTEP-MA | 2018-05-25 | Bill Pazella, ODEC | What happens to the taps? | BGE | Not addressing the taps.
SRRTEP-MA | 2018-05-25 | Bill Pazella, ODEC | If this is a reliability issue, concern about reliability. | BGE | 2 of the taps are single span, so issue is mitigated.
SRRTEP-MA | 2018-05-25 | Bill Pazella, ODEC | Headroom? | BGE | Will address in 2nd read. Unsure.
SRRTEP-MA | 2018-05-25 | Bill Pazella, ODEC | Relay changes? | BGE
SRRTEP-MA | 2018-05-25 | Ryan Dolan, AMP | Current circuit rating? | BGE | Don't have in front of me.
SRRTEP-MA | 2018-05-25 | Ryan Dolan, AMP | D/C or 6 wire? | BGE | D/C
SRRTEP-MA | 2018-05-25 | Kerry Neubrander | In Service date? | BGE | Covered earlier. Will update.
SRRTEP-MA | 2018-05-25 | Ryan Dolan, AMP | Was this modeling make in the current RTEP? | DPL | Not in 2022.
SRRTEP-MA | 2018-05-25 | Ryan Dolan, AMP | why did rating changed from last year to this year? | DPL | This work should be reflected. This is a relay limit. The relays are at Chestertown. They will be updated with this project and remove the limit.
SRRTEP-MA | 2018-05-25 | Ryan Dolan, AMP | But the rating went down. Bus 232202 and 23220? Rating issue is on another line.
SRRTEP-MA | 2018-05-25 | Ryan Dolan, AMP | Concern about why ratings change from year to year. Important for stakeholders to understand these changes. | PennElec | In service date is wrong.
SRRTEP-MA | 2018-05-25 | Ryan Dolan, AMP | Elaborate drivers for voltage update and double circuit. | PennElec | Constructed for 230kV but op at 115kV. Will be 6 wire for now. No current driver but planning for the future. Mulit outages in Erie area. Are "beyond criteria" so but real op issues. A lot of reactive control some voltage stays flat then drops suddenly. Prep for additional source into area.
SRRTEP-MA | 2018-05-25 | Ryan Dolan, AMP | Current limit of conductor, line? Future? | PennElec | Don't know conductor. Line limit is 214MVA. Will be 333MVA
SRRTEP-MA | 2018-05-25 | Ryan Dolan, AMP | Study at 115kV constr. And 230kV? | PennElec | Yes. When upgrade to 230kV, only one circ to 230kV other circ stays 115kV so don't have to upgrade subs.
SRRTEP-MA | 2018-05-25 | Ryan Dolan, AMP | steel lattice constr? | PennElec | Some steel lattice, some H-frame wood. May be a mix of structure types.
SRRTEP-MA | 2018-05-25 | Ryan Dolan, AMP | Performance issues? | PennElec | 14 sust, 29 Mom outages
SRRTEP-MA | 2018-05-25 | Ryan Dolan, AMP | Cause of outages? Statis issues? | PennElec | Don't have details. Have done a lot of "bandaid" repairs. Really need to address base condition.
SRRTEP-MA | 2018-05-25 | Ryan Dolan, AMP | Why is Aaron presenting? | PJM | Baseline.
SRRTEP-MA | 2018-05-25 | Ryan Dolan, AMP | Volt age currently? | PSEG | 26kV
SRRTEP-MA | 2018-05-25 | Ryan Dolan, AMP | Elim all 26kV in area? | PSEG | Not yet, but that is the plan.
SRRTEP-MA | 2018-05-25 | Ryan Dolan, AMP | 26kV is transmission? | PSEG | No, Distribution.
SRRTEP-MA | 2018-05-25 | Ryan Dolan, AMP | Within existing footprint? | PSEG | Yes. And will be very difficult and expensive.
SRRTEP-MA | 2018-05-25 | Ryan Dolan, AMP | 69kV 4 CB ring bus? | PSEG | 3 lines and 2 transformer, so min of 5.
SRRTEP-MA | 2018-05-25 | Ryan Dolan, AMP | Lines? | PSEG | Kearny-Madison, Greenville (from Bayonne),
SRRTEP-MA | 2018-05-25 | Ryan Dolan, AMP | studied impact of project? Any system impacts? Any impacts on other baselines? | PSEG | Yes. No. No.
SRRTEP-MA | 2018-05-25 | Ryan Dolan, AMP | Wenonah dist or trans? What is being retired? | AEP | Removal of some elements and moving load. 4 switch ring bus. Cost is transmission only.
SRRTEP-MA | 2018-05-25 | Ryan Dolan, AMP | transformer overload scenarios? Over load for loss of parallel transformer? | AEP | N-1-1 overload?
SRRTEP-MA | 2018-05-25 | Ryan Dolan, AMP | transformer size? | AEP | 41 MVA
SRRTEP-MA | 2018-05-25 | Ryan Dolan, AMP | Age & condition of transformer? | AEP | Overload issue, so condition is immaterial.
SRRTEP-MA | 2018-05-25 | Ryan Dolan, AMP | Eval for dist soln? | AEP | Done by dist. No option.
SRRTEP-MA | 2018-05-25 | Ryan Dolan, AMP | Not replace? | AEP | No, adding 3rd and reconfig high side.
SRRTEP-MA | 2018-05-25 | Bill Pazella, ODEC | conductor size and | AEP | 795ACSR, OPGW,
SRRTEP-MA | 2018-05-25 | Bill Pazella, ODEC | Load forecast? | AEP | No load growth forecast.
SRRTEP-MA | 2018-05-25 | Ryan Dolan, AMP | Conductor size & ratings, load? | AEC | 795 ACSR, 40MVA loading.
SRRTEP-MA | 2018-05-25 | Ryan Dolan, AMP | Load growth forecast? Excessive? | AEC | Adequate. Standard.
SRRTEP-MA | 2018-05-25 | Ryan Dolan, AMP | Separate circuits and ROW? | AEC | Yes, except for bridge.
SRRTEP-MA | 2018-05-25 | Ryan Dolan, AMP | Consider 23KV? Cheaper? | AEC | Presented last time. Yes by $2M.
SRRTEP-MA | 2018-05-25 | Ryan Dolan, AMP | Why not use same cheaper? | AEC | Because of weather experienced in the area.
SRRTEP-MA | 2018-05-25 | Ryan Dolan, AMP | Does est. of alternative include raising station? | AEC | Will get back.
SRRTEP-MA | 2018-05-25 | Ryan Dolan, AMP | Extend Loch Raven? | BGE | will discuss in next slide.
SRRTEP-MA | 2018-05-25 | Ryan Dolan, AMP | Have you considered...? | BGE | Sources are different. Some of those changes connect a weaker source to a stronger source, which presents flow/ops issues.
SRRTEP-MA | 2018-05-25 | Ryan Dolan, AMP | Look at system priorities (system planning) rather than addressing immediate issues? | BGE | Yes.
SRRTEP-MA | 2018-05-25 | Bill Pazella, ODEC | Where are problems that are protecting? | DPL | Wye Milles to Stevens
SRRTEP-MA | 2018-05-25 | Bill Pazella, ODEC | Why? | DPL | if fault on line, drop station.
SRRTEP-MA | 2018-05-25 | Bill Pazella, ODEC | only one source? | DPL | two sources.
SRRTEP-MA | 2018-05-25 | Ryan Dolan, AMP | transformers placed inside of same CB location? | DPL | No.
SRRTEP-MA | 2018-05-25 | Ryan Dolan, AMP | Line bus scheme? | DPL | Yes. Bus tie breaker? Removing circuit switchers.
SRRTEP-S | 2017-12-18 | Ryan Dolan, AMP | Current conductor | DOM | 477 ACSR
SRRTEP-S | 2017-12-18 | Ryan Dolan, AMP | Limiting Element? | DOM | Line is the current limiting element
SRRTEP-S | 2017-12-18 | Ryan Dolan, AMP | Station work? | DOM | Can not say at this time./Station equip typically rated well above conductor
SRRTEP-S | 2017-12-18 | Ryan Dolan, AMP | All changes come back to Committee | DOM | If have impact on cost or analysis
SRRTEP-S | 2017-12-18 | James Manning, NCEC | Will revisit this project later? Regional benefit to incr conductor | DOM | Upgrading to standard conductor. No need to incr.
SRRTEP-S | 2017-12-18 | James Manning, NCEC | ME or regional benefit to incr conductor. Although not needed for local load deliv. | PJM | No real procedure to do this analysis. Need to make assumptions, so not sure how to make these assumptions.
SRRTEP-S | 2017-12-18 | Ryan Dolan, AMP | ME analysis. Does EOL analysis consider turning on FSA units (do turn on ISA units). | PJM | "Wait and see" approach. So, aware of it, but don't necessarily impact. FSA incl in economic analysis. Should consider in local planning. FSA incl in econ model but not in RTEP model.
SRRTEP-S | 2017-12-18 | Ryan Dolan, AMP | Projected date for conversion to 230kV at the station | DOM | No date
SRRTEP-S | 2017-12-18 | Ryan Dolan, AMP | No high side circuit sw. | DOM | Correct
SRRTEP-S | 2017-12-18 | Ryan Dolan, AMP | The project is complete? Previously brought forward? | DOM | Yes. Distrib transformer is being installed in March 2018.
SRRTEP-S | 2017-12-18 | James Manning, NCEC | Project in-service now? | DOM | Yes.
SRRTEP-S | 2017-12-18 | James Manning, NCEC | No more N. American transformer? | DOM | No more at Kitty Hawk
SRRTEP-S | 2017-12-18 | Ryan Dolan, AMP | Willing to provide some past practice? Is there a sharing of knowledge? To learn from each other, standardize process. | PJM | Well beyond detail that has been captured before. Will need to continue the discussion.
SRRTEP-S | 2017-12-18 | Ryan Dolan, AMP | Age threshold for wave trap | DOM | 25 yrs.
SRRTEP-S | 2017-12-18 | Ryan Dolan, AMP | Short turn around time. Should allow more time, esp. for end of life | PJM | Understood but this level is low, nearly is an operation equipment.
SRRTEP-S | 2017-12-18 | James Manning, NCEC | Why bring this forward at all? Why not just O&M? | PJM | Brought forward because of rating change. If not, it might have just been an O&M project.
SRRTEP-S | 2017-12-18 | James Manning, NCEC | Prelim assumptions? | PJM | will do this in January.
SRRTEP-S | 2017-12-18 | James Manning, NCEC | If have areas of interest, can we add? | PJM | Yes.
SRRTEP-S | 2018-01-30 | James Manning, NCEC | Isn't 230 kV tap a more reasonable alt? | DOM | Not really feasible. Estab. New station. Upgrade 115 kV lines to 230kV. Permitting issues. Also update all customers to 230kV
SRRTEP-S | 2018-01-30 | Ryan Dolan, AMP | Proj to rebuild line & tap due to EOL | DOM | Yes, under constr.
SRRTEP-S | 2018-01-30 | Ryan Dolan, AMP | rebuild as D/C? Doesn't criteria require that? | DOM | No. We would look at it. But in this case its not cost effective.
SRRTEP-S | 2018-01-30 | Ryan Dolan, AMP | Wouldn't adding CB at Brinks be more cost effective? Was this considered? | DOM | Yes, we consider this.
SRRTEP-S | 2018-01-30 | Ryan Dolan, AMP | 4 mi extension. Under load loss criteria? | DOM | No issue.
SRRTEP-S | 2018-01-30 | James Manning, NCEC | Why 3 sw and where. | DOM
SRRTEP-S | 2018-01-30 | Ryan Dolan, AMP | How many taps? | DOM | only 1
SRRTEP-S | 2018-01-30 | Ryan Dolan, AMP | CBs on line? | DOM | at Perth, 4 CB ring.
SRRTEP-S | 2018-03-27 | James Manning, NCEC | Ratings? Clubhouse? | DOM | 5 - 6 MVA. Single breaker bus at Clubhouse.
SRRTEP-S | 2018-03-27 | Ryan Dolan, AMP | What will be the limiting element on circuit? | DOM | Don't have. How relevant?
SRRTEP-S | 2018-03-27 | Ryan Dolan, AMP | Will the new wave trap be the limiting element? | DOM | No. Why?
SRRTEP-S | 2018-03-27 | Ryan Dolan, AMP | Cascading tree analysis. Utilizes headroom. | DOM/PJM | Understand but haw is that relevant?/ Cascading tree analysis requires all the other elements to analyze.
SRRTEP-S | 2018-03-27 | James Manning, NCEC | Were is this being fed? Poe has multiple sources? | DOM | 115kV from Prince George. Yes, multiple sources.
SRRTEP-S | 2018-03-27 | Ryan Dolan, AMP | In construction? | DOM | No in engineering.
SRRTEP-S | 2018-03-27 | Ryan Dolan, AMP | Documenting questions? | PJM | Recording. Submit any outstanding questions.
SRRTEP-S | 2018-03-27 | Ryan Dolan, AMP | Outstanding questions. Publish meeting notes? | PJM | No. Will address outstanding questions.
SRRTEP-S | 2018-03-27 | Ryan Dolan, AMP | So any answers will be posted for all to see. | PJM | No. Still working on process. If ask question through PlanComm.
SRRTEP-S | 2018-03-27 | Ruth Price, DE Consumer Advocate | Should be able to standardize between all regions. When will we get together. | PJM | We are striving for standardized slides. Discussing how to communicate. A challenge is the open issues at FERC. Without direction.
SRRTEP-S | 2018-03-27 | Ruth Price, DE Consumer Advocate | What do you mean by standardize? | PJM | Not all parties agree what is the basic info.
SRRTEP-S | 2018-03-27 | Ryan Dolan, AMP | Presented info on standard slides. Shared at PC. Told working on it internally. When will PJM bring to stakeholders? | PJM | We have engaged in those discussions in multiple ways. Some of the factors are external and not within PJM's control. Can't really finalize until FERC issues are complete. Template will be vetted by all stakeholders.
SRRTEP-S | 2018-03-27 | Ryan Dolan, AMP | Anything that prevents PJM from gathering info? Perhaps special meetings. Not sure there is time to do this within the PC/TEAC meetings. | PJM | Will take that back to senior mgmt.
SRRTEP-S | 2018-03-27 | Ruth Price, DE Consumer Advocate | I don't see what prohibits PJM from working toward this. | PJM | Will look into it. Do want to look into impacts of extra work.
SRRTEP-S | 2018-05-30 | Mark Ringhausen, ODEC | Rating of line? | DOM
SRRTEP-S | 2018-05-30 | Mark Ringhausen, ODEC | CB/Switches condition? | DOM | Gear op worn, hot spots on switches so will replace.
SRRTEP-S | 2018-05-30 | Mark Ringhausen, ODEC | transformer serving load? | DOM | None owned by Dom. Is w
SRRTEP-S | 2018-05-30 | Mark Ringhausen, ODEC | Why just presented now? | DOM | Op issues getting worse. Also, had time available to
SRRTEP-S | 2018-05-30 | James Manning, NCEC | Are these switches wide spread? | DOM | There are others through out the system
SRRTEP-S | 2018-05-30 | James Manning, NCEC | Upgraded relaying? Improved fault detection? | DOM | Yes.
SRRTEP-S | 2018-05-30 | Ryan Dolan, AMP | Is there no space, is that driver? | DOM | Yes. Also shared with Appalachian. Coord is challenging.
SRRTEP-S | 2018-05-30 | Ryan Dolan, AMP | Who will own the new ctrl house? | DOM | Dom. Appalachian not planning new work.
SRRTEP-S | 2018-05-30 | Mark Ringhausen, ODEC | Show what will impact rates and what customer will pay. | PJM | Ok. To update on 2nd read?
SRRTEP-S | 2018-05-30 | Mark Ringhausen, ODEC | Any line upgrades or rating changes? | DOM | No.
SRRTEP-S | 2018-05-30 | Mark Ringhausen, ODEC | Where is load moving? | DOM | All within station.
SRRTEP-W | 2017-12-18 | Ryan Dolan, AMP | Meaningful follow up on outstanding questions | PJM | Dealing with how to answer. Address process in parallel.
SRRTEP-W | 2017-12-18 | Ryan Dolan, AMP | Concern that projects are not getting enough opportunity. Appreciate the discussions in private but all stakeholders would benefit. | AEP | Got 50 questions from AMP 7 business days. Working through the questions. Will take some time.
SRRTEP-W | 2017-12-18 | Ed Tatum, AMP | Believe that need to address info before entered into PJM base model. | PJM | Legal is looking that legal obligations of supplemental review. Need to address when a project is "final".
SRRTEP-W | 2017-12-18 | Ryan Dolan, AMP | Load included in 2018 model
SRRTEP-W | 2017-12-18 | Ryan Dolan, AMP | Good to know when it will be submitted. | ComEd
SRRTEP-W | 2017-12-18 | Ryan Dolan, AMP | Request one-line, conceptual? | PJM/ComEd/PJM | Can request. But defer to ComEd./ Make request through PJM./ Still figuring out how to handle the request
SRRTEP-W | 2017-12-18 | Ryan Dolan, AMP | Do no harm analysised? Idev's available? | PJM | Analyzed, yes. Not sure if idev available for this project.
SRRTEP-W | 2017-12-18 | Ryan Dolan, AMP | Threshold for ring vs. straight bus? | ComEd | ring bus at minimum. No new subs straight bus.
SRRTEP-W | 2017-12-18 | Ryan Dolan, AMP | Threshold for connections to trans system. | Comed | No threshold, independent review.
SRRTEP-W | 2017-12-18 | Ryan Dolan, AMP | Entered in 2018 case? | ComEd | Not yet.
SRRTEP-W | 2017-12-18 | Ryan Dolan, AMP | So no study? | ComEd | Existing load, relocating from dist to trans load.
SRRTEP-W | 2017-12-18 | Ryan Dolan, AMP | Load is moving? Has PJM reviewed? | PJM | Yes. Review before present.
SRRTEP-W | 2017-12-18 | Ryan Dolan, AMP | Is it in the 2018 case? | PJM | it has been in model.
SRRTEP-W | 2017-12-18 | Ryan Dolan, AMP | Any additional work? | ComEd | No
SRRTEP-W | 2017-12-18 | Bill Pazella, ODEC | Load in the area evaluated? So, don't need to expand in the future |  | 36 MVA
SRRTEP-W | 2017-12-18 | Ryan Dolan, AMP | How cap bank connected to sta? |  | CB.
SRRTEP-W | 2017-12-18 | Ryan Dolan, AMP | Size? |  | More than big enough.
SRRTEP-W | 2017-12-18 | Bill Pazella, ODEC | Current and new ratings? | ComEd | Not in front of me.
SRRTEP-W | 2017-12-18 | Ryan Dolan, AMP | Question was asked at the last meeting? When can we expect the answer? | PJM | We don't need the info at this time, so appreciate CE supply the info at this time.
SRRTEP-W | 2017-12-18 | Ryan Dolan, AMP | See a need to increase cooling? | PJM | No.
SRRTEP-W | 2017-12-18 | Ryan Dolan, AMP | Redundant system? | ComEd | No, additional cooling.
SRRTEP-W | 2017-12-18 | Ryan Dolan, AMP | Assoc. with prior project to transfer load to Bellwood? | ComEd | Yes, also most heavily loaded transformer, so improve overall system reliability.
SRRTEP-W | 2017-12-18 | Ryan Dolan, AMP | If load not transferred, would cap bank be upgraded? | ComEd | Yes
SRRTEP-W | 2017-12-18 | Ryan Dolan, AMP | Phase shift. Explain? | ComEd | Loading on McCook transformer, limits the ability to adjust PAR
SRRTEP-W | 2017-12-18 | Ryan Dolan, AMP | Radial lines in AEP rate base? | AEP | Yes. Unless owned by whole customer, the lines should be in the rate base.
SRRTEP-W | 2017-12-18 | Ryan Dolan, AMP | Est. date when should have response? | AEP | Expect 2nd or 3rd week of Jan. Working with PJM. Consulting with legal.
SRRTEP-W | 2017-12-18 | Ryan Dolan, AMP | will have detailed breakdown of alternatives? | AEP | Will look at but don't do detailed estimates for alt.
SRRTEP-W | 2017-12-18 | Ryan Dolan, AMP | No add'l other than CB replacement? | AEP | Correct. There are several IPP interconnects pending in the area.
SRRTEP-W | 2017-12-18 | Ryan Dolan, AMP | Overlap zones of protection with transformer 1 | AEP | transformer & bus overlapping protection. Not ideal but within standards.
SRRTEP-W | 2017-12-18 | Bill Pazella, ODEC | DICM going in. Which line item has that cost. | AEP | DICM is part of distribution cost.
SRRTEP-W | 2017-12-18 | Ryan Dolan, AMP | Line feeding Anaconda Line Tap station. Line retired? | AEP | Correct. However, cannot commit today, need to work with 2nd customer.
SRRTEP-W | 2017-12-18 | Ryan Dolan, AMP | customer providing land at their cost? | AEP | Trying but an existing customer.
SRRTEP-W | 2017-12-18 | Ryan Dolan, AMP | Why build to 69kV? | AEP | That is the standard.
SRRTEP-W | 2017-12-18 | Bill Pazella, ODEC | Mix of baseline & supplemental #'s. Mixing them? | AEP | No. baseline exists. But trying to take care additional work at the same time.
SRRTEP-W | 2017-12-18 | Ryan Dolan, AMP | CB#M not in baseline? | AEP | No, only transformer included. All other work is supplemental
SRRTEP-W | 2017-12-18 | Ryan Dolan, AMP | Depreciation of CB? Also mortality curve on CB? | AEP | Not clear, parts depreciated a different rates.
SRRTEP-W | 2017-12-18 | Ryan Dolan, AMP | CB type? | AEP | SF-6 type.
SRRTEP-W | 2017-12-18 | Ed Tatum, AMP | Last year AEP held several meetings last year. They were good. How does this fit with the local planning process. | AEP | Will address to legal. Seems to be redundant with this process.
SRRTEP-W | 2017-12-18 | Ryan Dolan, AMP | transformer; distrib or transm? | AEP | Have that question from you. Need to follow up.
SRRTEP-W | 2017-12-18 | Ryan Dolan, AMP | In-service? | AEP | Not sure.
SRRTEP-W | 2017-12-18 | Ryan Dolan, AMP | Land purchase T or D | AEP | Should be D
SRRTEP-W | 2017-12-18 | Ryan Dolan, AMP | high side switcher, T or D? | AEP | High side. Will clarify.
SRRTEP-W | 2017-12-18 | Ryan Dolan, AMP | Why CB and not MOAB? | AEP | Long line with existing MOABs on line. Cost is only the T work to be done.
SRRTEP-W | 2017-12-18 | Ryan Dolan, AMP | stations and | AEP | Hazard Sta. not incl.
SRRTEP-W | 2017-12-18 | Ryan Dolan, AMP | share all of calc's | AEP | Atlanta airport shows the concern about how much to understand. Non-transferable load at station.
SRRTEP-W | 2017-12-18 | Ryan Dolan, AMP | project in-service? | AEP | looks like it will be in 2018.
SRRTEP-W | 2017-12-18 | Ryan Dolan, AMP | Retire GE FK CB's. Use for spares? | AEP | Yes. But
SRRTEP-W | 2017-12-18 | Ryan Dolan, AMP | Any land expansion required? | AEP | No.
SRRTEP-W | 2017-12-18 | Ryan Dolan, AMP | Each line to a CB position. | AEP | Yes, in breaker and half config.
SRRTEP-W | 2017-12-18 | Ryan Dolan, AMP | Replacement CB's | AEP | 50kA
SRRTEP-W | 2017-12-18 | Ryan Dolan, AMP | why upgrade to 63kA | AEP | standard rating.
SRRTEP-W | 2017-12-18 | Ryan Dolan, AMP | Request Aspen models and results? | AEP | yes.
SRRTEP-W | 2017-12-18 | Ryan Dolan, AMP | Practice with transformer that retire? | AEP | Assess but will scrap these, due to age.
SRRTEP-W | 2017-12-18 | Ryan Dolan, AMP | transformer practices? | AEP | Reviewing what can share. Will have experts provide presentation by April.
SRRTEP-W | 2017-12-18 | Ryan Dolan, AMP | Consistency question. By lines off busses.
SRRTEP-W | 2017-12-18 | Ryan Dolan, AMP | Not optimal to serve load from another util? | AEP | Goal to provide station service from transmission.
SRRTEP-W | 2017-12-18 | Ryan Dolan, AMP | How many fault ops on CB #B | AEP | 9 operations.
SRRTEP-W | 2017-12-18 | Ryan Dolan, AMP | Manuf recommended. | AEP | Below, but just one factor.
SRRTEP-W | 2017-12-18 | Ryan Dolan, AMP | PCB content? | AEP | Suspected.
SRRTEP-W | 2017-12-18 | Ryan Dolan, AMP | Are we going to get answers? | AEP | will answer.
SRRTEP-W | 2017-12-18 | Ryan Dolan, AMP | Arrangement that requires 6 138 kV CB | AEP | breaker and a half. Customer is sensitive to outages.
SRRTEP-W | 2017-12-18 | Ryan Dolan, AMP | Not 2 zones of protection? Are you applying this rule consistently? | AEP | Yes.
SRRTEP-W | 2017-12-18 | Ryan Dolan, AMP | Wilford station is consistent? | AEP | Completely different arrangement.
SRRTEP-W | 2017-12-18 | Ryan Dolan, AMP | projects still coming back? | PJM | No, were not planning to bring them back. Questions will be answered.
SRRTEP-W | 2017-12-18 | Ryan Dolan, AMP | When answer to ques? | PJM | When have answers. Asked for a lot of info. Will take time to compile.
SRRTEP-W | 2017-12-18 | Mike Gahimer, IN Util Consumer Council | What if the answers provoke additional questions? | PJM | Questions and answer will continue. Will come back if needed
SRRTEP-W | 2017-12-18 | Ryan Dolan, AMP | Want project come back until get one line diagrams. | AEP | AEP has obligation to proceed. Do not hear objection to need. Ques. Related to if rules applied consistently. This is a min. config.
SRRTEP-W | 2017-12-18 | Mike Gahimer, IN Util Consumer Council | Who pays for what? | AEP | Costs shown here is only the ratepayer costs. Not should is costs paid by GM.
SRRTEP-W | 2017-12-18 | Ryan Dolan, AMP | Age of CB 32, 34 | AEP | 1974
SRRTEP-W | 2017-12-18 | Ryan Dolan, AMP | would replace if less than 10 fault ops? | AEP | One of many factors.
SRRTEP-W | 2017-12-18 | Mike Gahimer, IN Util Consumer Council | To what extent can this be done under O&M? Why this year? | AEP | Lots of lines. Hard to cover all under O&M. Need to do something. Try to get the ones in the worst condition first. Also need to consider the risk to the system &
SRRTEP-W | 2017-12-18 | Ryan Dolan, AMP | Any trees hazards? | AEP | Will look up. 69kV lines built with 30-40 ft ROW width. That was the std.
SRRTEP-W | 2017-12-18 | Ryan Dolan, AMP | 24 open struct. How many are trees? Where? Etc.? | AEP
SRRTEP-W | 2017-12-18 | Ryan Dolan, AMP | rebuilt in existing ROW? | AEP | For the most part.
SRRTEP-W | 2017-12-18 | Ryan Dolan, AMP | Are opens at Sharples station? | AEP | Not sure.
SRRTEP-W | 2017-12-18 | Ryan Dolan, AMP | interested in details of all opens | AEP | This is considered. All TO have to consider if that info can be sent to all stakeholders.
SRRTEP-W | 2017-12-18 | Ryan Dolan, AMP | Hold projects until send this info? | AEP | No. Already providing more info than and TO has provided in N.A. AEP has obligation to operate its grid.
SRRTEP-W | 2017-12-18 | Ed Tatum, AMP | If confidential, can have discussion in closed forum? | AEP | That would help but there is also an issue with handling the volume of info.
SRRTEP-W | 2017-12-18 | Ryan Dolan, AMP | Hopkins-Sharples, radial service? | AEP | No policy on radial line mile load std yet.
SRRTEP-W | 2017-12-18 | Mike Gahimer, IN Util Consumer Council | How long switches have been in-operable? | AEP | Check every 5 yrs. Address when identified.
SRRTEP-W | 2017-12-18 | Mike Gahimer, IN Util Consumer Council | No way to know without visit line? | AEP | Yes. Trying drones.
SRRTEP-W | 2017-12-18 | Bill Pazella, ODEC | Build to 138kV std? Time line to change over? | AEP | No but discussing with customers.
SRRTEP-W | 2017-12-18 | Ryan Dolan, AMP | Justification to upgrade? | AEP | conversations with customers. They have a variety of reasons. Small delta.
SRRTEP-W | 2017-12-18 | Mike Gahimer, IN Util Consumer Council | Customers paying for incremental cost? | AEP | No,
SRRTEP-W | 2017-12-18 | Ryan Dolan, AMP | Rational? Any customer comes to AEP and asks for upgrade and you do it? | AEP | Depends.
SRRTEP-W | 2017-12-18 | Mike Gahimer, IN Util Consumer Council | Unique needs. Why does the customer not pay for upgrade rather than all ratepayers. | AEP | Each state has its own rules. The FERC has rules too.
SRRTEP-W | 2017-12-18 | Ryan Dolan, AMP | If customer connects in OH, state has rules for who pays for what. | AEP | Our obligation to follow up on. On Sharples, it is a coal customer. By state tariff is considered a temp customer.
SRRTEP-W | 2017-12-18 | Ryan Dolan, AMP | Customer still there? | AEP | Yes.
SRRTEP-W | 2017-12-18 | Ryan Dolan, AMP | replacing then installing new? | AEP | One for one replacement.
SRRTEP-W | 2017-12-18 | Ryan Dolan, AMP | Project already in construction when brought to committee. | AEP | Disagree. Brought forward in October. Has taken time to bring forward. Heart rot is a serious safety issue. Had to move quickly.
SRRTEP-W | 2017-12-18 | Ryan Dolan, AMP | 3 river sta, driver? | AEP | Aging, cannot rebuild in location. Build in the clear. Also, reduces downtime.
SRRTEP-W | 2017-12-18 | Erik Hanser, Mich PUC | wood or steel poles? | AEP | steel.
SRRTEP-W | 2017-12-18 | Ryan Dolan, AMP | Consider adding transformer at Hydramatic and retiring some lines? | AEP
SRRTEP-W | 2017-12-18 | Ryan Dolan, AMP | Retire MoorePark to Hdyramatic. Serve from 138kV. | AEP/PJM | area designed for single conting. As infrastructure ages, seeing single conting. Don't see lines in studies, because peaks Sept, October. /Don't see advantage. Can discuss offline.
SRRTEP-W | 2017-12-18 | Bill Pazella, ODEC | supplemental number correct? | PJM | yes.
SRRTEP-W | 2017-12-18 | Ryan Dolan, AMP | Operate to N-1-1? How operate in this system? | PJM | Operates to N-1. Can dispatch if an issue.
SRRTEP-W | 2017-12-18 | Ryan Dolan, AMP | Any dynamic studies of new condenser? | PJM | No.
SRRTEP-W | 2017-12-18 | Ryan Dolan, AMP | Will PJM? | PJM/AEP | Not planned to. Rely on AEP./Condensor still needed? Yes.
SRRTEP-W | 2017-12-18 | Ryan Dolan, AMP | Provide a time series plot of condenser? | AEP | consider. PJM will not see in their studies as it is an operational issues. Not a dynamics issues.
SRRTEP-W | 2017-12-18 | Ryan Dolan, AMP | Dynamics can provide insights. | PJM | this is a local issue. PJM is not the expert in this area.
SRRTEP-W | 2017-12-18 | Ryan Dolan, AMP | Has there been a dynamic study? | AEP | No, it is not a dynamic issue.
SRRTEP-W | 2017-12-18 | Ryan Dolan, AMP | how know it is sized correctly? | AEP | because it handles the need. Anything more would be oversizing.
SRRTEP-W | 2017-12-18 | Ryan Dolan, AMP | PJM will want to confirm that condenser is appropriate size.
SRRTEP-W | 2017-12-18 | Ryan Dolan, AMP | PJM help understand the project. | AEP | This is basic planning. You should be able to model yourself.
SRRTEP-W | 2017-12-18 | Bill Pazella, ODEC | If fully reimbursable, does it need to be here? | PJM | Ask for projects that impact models or generate Ops outage tickets.
SRRTEP-W | 2017-12-18 | Ryan Dolan, AMP | Cost is 100% reimbursable? | ATSI | Yes. And it improves reliability.
SRRTEP-W | 2017-12-18 | Ryan Dolan, AMP | Will follow up with an alternative plan. Think will improve reliability. | ATSI | Yes. Dave mentioned it. Many straight bus configs on system. Looking to improve reliability.
SRRTEP-W | 2017-12-18 | Ryan Dolan, AMP | Only concern is poss. Loss of both muni feeds. Ideally would like to restore one feed. | ATSI | See that concern. Will pass that on.
SRRTEP-W | 2017-12-18 | Ryan Dolan, AMP | Modeling questions & one lines. Follow-up line condition questions. Like the sectionalizing scheme. | ATSI | 7 outages over last 3 yrs.
SRRTEP-W | 2017-12-18 | Ryan Dolan, AMP | Why CB and not switcher? | ATSI | Not part of standards.
SRRTEP-W | 2017-12-18 | Ryan Dolan, AMP | Work on 138-12kV side? | ATSI | Will note.
SRRTEP-W | 2017-12-18 | Ryan Dolan, AMP | Info on future plans. Need to prep for rate increases. | ATSI | Has been made clear and working to improve. Will provide one-line
SRRTEP-W | 2017-12-18 | Ryan Dolan, AMP | Condition asses, switching, etc. | ATSI | will do. These projects are planning driven, not condition-based.
SRRTEP-W | 2017-12-18 | Ryan Dolan, AMP | Line outages?
SRRTEP-W | 2017-12-18 | Ryan Dolan, AMP | 138kV line from Avery. Is there a power injection? | ATSI | No sure, Dave will follow up.
SRRTEP-W | 2017-12-18 | Ryan Dolan, AMP | For Prospect Muni, Is tap into sub in scope? | ATSI | Yes it is.
SRRTEP-W | 2017-12-18 | Ryan Dolan, AMP | Concern that project is under construction. | ATSI | Traditional, include reliability project, not impedance projects. So catching up.
SRRTEP-W | 2017-12-18 | Ryan Dolan, AMP | Wood or steel? | ATSI | Will follow up.
SRRTEP-W | 2017-12-18 | Ryan Dolan, AMP | Age of towers. | ATSI | Based on condition not age.
SRRTEP-W | 2017-12-18 | Ryan Dolan, AMP | New bus is not trans? | ComEd | No, high voltage distrib. Radial line.
SRRTEP-W | 2017-12-18 | Ryan Dolan, AMP | Any other associated work? | ComEd | Correct.
SRRTEP-W | 2017-12-18 | Ryan Dolan, AMP | what aspect of PRC-023 do the relays fail. | ComEd | Not sure. Will need to follow up.
SRRTEP-W | 2017-12-18 | Ryan Dolan, AMP | Just line config work? | DEOK | yes.
SRRTEP-W | 2017-12-18 | Ryan Dolan, AMP | Current conductor and new size? | DEOK | Not sure. Planning only designates rating.
SRRTEP-W | 2017-12-18 | Ryan Dolan, AMP | Gen retirement? | DEOK | Comes up frequently. Not sure this particular time. This is an aging project. Planning has directed the increased rating.
SRRTEP-W | 2017-12-18 | Ryan Dolan, AMP | Does the "parallel" line have issues? Looked into retiring the line? | DEOK | No, No.
SRRTEP-W | 2017-12-18 | Ryan Dolan, AMP | All wood poles from 1912? | AEP | Majority yes.
SRRTEP-W | 2017-12-18 | Ryan Dolan, AMP | Under construction? | AEP | Just started.
SRRTEP-W | 2017-12-18 | Ryan Dolan, AMP | Conductor size? | AEP | 556 is min. Many requests so incr.
SRRTEP-W | 2017-12-18 | Ryan Dolan, AMP | Steel or wood? Why? | AEP | Steel. That is the standard.
SRRTEP-W | 2017-12-18 | Ryan Dolan, AMP | Does PJM have a standard about poles? | PJM | Ther e is a standard. Not sure what it says.
SRRTEP-W | 2017-12-18 | Ed Tatum, AMP | Rebuild 11.3 or 12.8 mi? | AEP | 11.3mi. Will address that 1.5 mi in a separate project. Looking to coord with another project.
SRRTEP-W | 2017-12-18 | Ryan Dolan, AMP | Already know there will be another project? | AEP | Not sure.
SRRTEP-W | 2017-12-18 | Ed Tatum, AMP | As a process improvement , need to get the projects to the committee before they are under construction. | PJM | Understood. But things happen.
SRRTEP-W | 2017-12-18 | Ryan Dolan, AMP | Line retirement? See no issues. Have AEP or PJM studied? | AEP | A lot of develop potential in the area, ~200MW. Also, had a load shed issue in the area.
SRRTEP-W | 2017-12-18 | Mike Gahimer, IN Util Consumer Council | May not be needed immediately but is long term. So don't need to do this immediately, i.e., it does not need to be under construction at the time of the first read. | AEP | Performing inspections 8-10 yrs. Recent study identified serious deficiencies.
SRRTEP-W | 2017-12-18 | Ryan Dolan, AMP | Just rebuilt Poston-Hocking a few years ago. Why not rebuild at the same time? | AEP | Don't have info in front of them.
SRRTEP-W | 2017-12-18 | Ed Tatum, AMP | How many customers? | AEP | Serving one customer, Good Hope
SRRTEP-W | 2017-12-18 | Ryan Dolan, AMP | Consulted with customer before start work. | AEP | Not sure.
SRRTEP-W | 2017-12-18 | Bill Pazella, ODEC | 5 CB, How many to city? Age of CB? | AEP | split bus with tie breaker. 1974
SRRTEP-W | 2018-01-08 | Ryan Dolan, AMP | Arrangement that requires 6 138 kV CB | AEP | breaker and a half. Customer is sensitive to outages.
SRRTEP-W | 2018-01-08 | Ryan Dolan, AMP | Not 2 zones of protection? Are you applying this rule consistently? | AEP | Yes.
SRRTEP-W | 2018-01-08 | Ryan Dolan, AMP | Wilford station is consistent? | AEP | Completely different arrangement.
SRRTEP-W | 2018-01-08 | Ryan Dolan, AMP | projects still coming back? | PJM | No, were not planning to bring them back. Questions will be answered.
SRRTEP-W | 2018-01-08 | Ryan Dolan, AMP | When answer to ques? | PJM | When have answers. Asked for a lot of info. Will take time to compile.
SRRTEP-W | 2018-01-08 | Mike Gahimer, IN Util Consumer Council | What if the answers provoke additional questions? | PJM | Questions and answer will continue. Will come back if
SRRTEP-W | 2018-01-08 | Ryan Dolan, AMP | Want project come back until get one line diagrams. | PJM/AEP | ok./ AEP has obligation to proceed. Do not hear objection to need. Ques. Related to if rules applied consistently. This is a min. config.
SRRTEP-W | 2018-01-08 | Mike Gahimer, IN Util Consumer Council | Who pays for what? | AEP | Costs shown here is only the ratepayer costs. Not should is costs paid by GM.
SRRTEP-W | 2018-01-08 | Ryan Dolan, AMP | Age of CB 32, 34?
SRRTEP-W | 2018-01-08 | Ryan Dolan, AMP | would replace if less than 10 fault ops? | AEP | One of many factors.
SRRTEP-W | 2018-01-08 | Mike Gahimer, IN Util Consumer Council | To what extent can this be done under O&M? Why this year? | AEP | Lots of lines. Hard to cover all under O&M. Need to do something. Try to get the ones in the worst condition first. Also need to consider the risk to the system &
SRRTEP-W | 2018-01-08 | Ryan Dolan, AMP | Any trees hazards? | AEP | Will look up. 69kV lines built with 30-40 ft ROW width. That was the std.
SRRTEP-W | 2018-01-08 | Ryan Dolan, AMP | 24 open struct. How many are trees? Where? Etc.? | AEP
SRRTEP-W | 2018-01-08 | Ryan Dolan, AMP | rebuilt in existing ROW? | AEP | For the most part.
SRRTEP-W | 2018-01-08 | Ryan Dolan, AMP | Are opens at Sharples station? | AEP | Not sure.
SRRTEP-W | 2018-01-08 | Ryan Dolan, AMP | interested in details of all opens | AEP | This is considered. All TO have to consider if that info can be sent to all stakeholders.
SRRTEP-W | 2018-01-08 | Ryan Dolan, AMP | Hold projects until send this info? | AEP | No. Already providing more info than and TO has provided in N.A. AEP has obligation to operate its grid.
SRRTEP-W | 2018-01-08 | Ed Tatum, AMP | If confidential, can have discussion in closed forum? | AEP | That would help but there is also an issue with handling the volume of info.
SRRTEP-W | 2018-01-08 | Ryan Dolan, AMP | Hopkins-Sharples, radial service? | AEP | No policy on radial line mile load std yet.
SRRTEP-W | 2018-01-08 | Mike Gahimer, IN Util Consumer Council | How long switches have been operable? | AEP | Check every 5 yrs. Address when identified.
SRRTEP-W | 2018-01-08 | Mike Gahimer, IN Util Consumer Council | No way to know without visit line? | AEP | Yes. Trying drones.
SRRTEP-W | 2018-01-08 | Bill Pazella, ODEC | Build to 138kV std? Time line to change over? | AEP | No but discussing with customers.
SRRTEP-W | 2018-01-08 | Ryan Dolan, AMP | Justification to upgrade? | AEP | conversations with customers. They have a variety of reasons. Small delta.
SRRTEP-W | 2018-01-08 | Mike Gahimer, IN Util Consumer Council | Customers paying for incremental cost? | AEP | No,
SRRTEP-W | 2018-01-08 | Ryan Dolan, AMP | Rational? Any customer comes to AEP and asks for upgrade and you do it? | AEP | Depends.
SRRTEP-W | 2018-01-08 | Mike Gahimer, IN Util Consumer Council | Unique needs. Why does the customer not pay for upgrade rather than all ratepayers. | AEP | Each state has its own rules. The FERC has rules too.
SRRTEP-W | 2018-01-08 | Ryan Dolan, AMP | If customer connects in OH, state has rules for who pays for what. | AEP | Our obligation to follow up on. On Sharples, it is a coal customer. By state tariff is considered a temp customer.
SRRTEP-W | 2018-01-08 | Ryan Dolan, AMP | Customer still there? | AEP | Yes.
SRRTEP-W | 2018-01-08 | Ryan Dolan, AMP | replacing then installing new? | AEP | One for one replacement.
SRRTEP-W | 2018-01-08 | Ryan Dolan, AMP | Project already in construction when brought to committee. | AEP | Disagree. Brought forward in October. Has taken time to bring forward. Heart rot is a serious safety issue. Had to move quickly.
SRRTEP-W | 2018-01-08 | Ryan Dolan, AMP | 3 river sta, driver? | AEP | Aging, cannot rebuild in location. Build in the clear. Also, reduces downtime.
SRRTEP-W | 2018-01-08 | Erik Hanser, Mich PUC | wood or steel poles? | AEP | steel.
SRRTEP-W | 2018-01-08 | Ryan Dolan, AMP | Consider adding transformer at Hydramatic and retiring some lines? | AEP
SRRTEP-W | 2018-01-08 | Ryan Dolan, AMP | Retire MoorePark to Hdyramatic. Serve from 138kV. | AEP | area designed for single conting. As infrastructure ages, seeing single conting. Don't see lines in studies, because peaks Sept, October. Don't see advantage. Can discuss offline.
SRRTEP-W | 2018-01-08 | Bill Pazella, ODEC | supplemental number correct? | PJM | yes.
SRRTEP-W | 2018-01-08 | Ryan Dolan, AMP | Operate to N-1-1? How operate in this system? | PJM | Operates to N-1. Can dispatch if an issue.
SRRTEP-W | 2018-01-08 | Ryan Dolan, AMP | Any dynamic studies of new condenser? | PJM | No.
SRRTEP-W | 2018-01-08 | Ryan Dolan, AMP | Will PJM? | PJM | Not planned to. Rely on AEP.
SRRTEP-W | 2018-01-08 | Ryan Dolan, AMP | Condensor still needed? | AEP | Yes.
SRRTEP-W | 2018-01-08 | Ryan Dolan, AMP | Provide a time series plot of condenser? | AEP | consider. PJM will not see in their studies as it is an operational issues. Not a dynamics issues.
SRRTEP-W | 2018-01-08 | Ryan Dolan, AMP | Dynamics can provide insights. | PJM | this is a local issue. PJM is not the expert in this area.
SRRTEP-W | 2018-01-08 | Ryan Dolan, AMP | Has there been a dynamic study? | AEP | No, it is not a dynamic issue.
SRRTEP-W | 2018-01-08 | Ryan Dolan, AMP | how know it is sized correctly? | AEP | because it handles the need. Anything more would be oversizing. installing 200 cap. New cap has an overexcited up to 250. condenser does not run continuously.
SRRTEP-W | 2018-01-08 | Ryan Dolan, AMP | PJM will want to confirm that condenser is appropriate size. PJM help understand the project. | PJM | Not sure what is the question. This is basic planning. You should be able to model yourself.
SRRTEP-W | 2018-01-08 | Bill Pazella, ODEC | If fully reimbursable, does it need to be here? | PJM | Ask for projects that impact models or generate Ops outage tickets.
SRRTEP-W | 2018-01-08 | Ryan Dolan, AMP | Cost is 100% reimbursable? | ATSI | Yes. And it improves reliability.
SRRTEP-W | 2018-01-08 | Ryan Dolan, AMP | Will follow up with an alternative plan. Think will improve reliability. | ATSI | Yes. Dave mentioned it.
SRRTEP-W | 2018-01-08 | Ryan Dolan, AMP | Only concern is poss. Loss of both muni feeds. Ideally would like to restore one feed. | ATSI | See that concern. Will pass that on.
SRRTEP-W | 2018-01-08 | Ryan Dolan, AMP | Modeling questions & one lines. Follow-up line condition questions. Like the sectionalizing scheme. | ATSI | 7 outages over last 3 yrs.
SRRTEP-W | 2018-01-08 | Ryan Dolan, AMP | Why CB and not switcher? | ATSI | Not part of standards.
SRRTEP-W | 2018-01-08 | Ryan Dolan, AMP | Work on 138-12kV side? | ATSI | Will note.
SRRTEP-W | 2018-01-08 | Ryan Dolan, AMP | Info on future plans. Need to prep for rate increases. | ATSI | Has been made clear and working to improve. Will provide one-line.
SRRTEP-W | 2018-01-08 | Ryan Dolan, AMP | Condition asses, switching, etc. | ATSI | will do. These projects are planning driven, not condition-based.
SRRTEP-W | 2018-01-08 | Ryan Dolan, AMP | 138kV line from Avery. Is there a power injection? | ATSI | No sure, Dave will follow up.
SRRTEP-W | 2018-01-08 | Ryan Dolan, AMP | For Prospect Muni, Is tap into sub in scope? | ATSI | Yes it is.
SRRTEP-W | 2018-01-08 | Ryan Dolan, AMP | Concern that project is under construction. | ATSI | Traditional, include reliability project, not impedance projects. So catching up.
SRRTEP-W | 2018-01-08 | Ryan Dolan, AMP | Wood or steel? | ATSI | Will follow up.
SRRTEP-W | 2018-01-08 | Ryan Dolan, AMP | Age of towers. | ATSI | Based on condition not age.
SRRTEP-W | 2018-01-08 | Ryan Dolan, AMP | New bus is not trans? | ComEd | No, high voltage distrib. Radial line.
SRRTEP-W | 2018-01-08 | Ryan Dolan, AMP | Any other associated work? | ComEd | Correct.
SRRTEP-W | 2018-01-08 | Ryan Dolan, AMP | what aspect of PRC-023 do the relays fail. | ComEd | Not sure. Will need to follow up.
SRRTEP-W | 2018-01-08 | Ryan Dolan, AMP | Just line config work? | DEOK | yes.
SRRTEP-W | 2018-01-08 | Ryan Dolan, AMP | Current conductor and new size? | DEOK | Not sure. Planning only designates rating.
SRRTEP-W | 2018-01-08 | Ryan Dolan, AMP | Gen retirement? | DEOK | Comes up frequently. Not sure this particular time. This is an aging project. Planning has directed the increased rating.
SRRTEP-W | 2018-01-08 | Ryan Dolan, AMP | Does the "parallel" line have issues. Looked into retiring the line. | DEOK | No, No.
SRRTEP-W | 2018-01-08 | Ryan Dolan, AMP | All wood poles from 1912? | AEP | Majority yes.
SRRTEP-W | 2018-01-08 | Ryan Dolan, AMP | Under construction? | AEP | Just started.
SRRTEP-W | 2018-01-08 | Ryan Dolan, AMP | Conductor size? | AEP | 556 is min. Many requests so incr.
SRRTEP-W | 2018-01-08 | Ryan Dolan, AMP | Steel or wood? Why? | AEP | Steel. That is the standard.
SRRTEP-W | 2018-01-08 | Ryan Dolan, AMP | Does PJM have a standard about poles? | PJM | Ther e is a standard. Not sure what it says.
SRRTEP-W | 2018-01-08 | Ed Tatum, AMP | Rebuild 11.3 or 12.8 mi? | AEP | 11.3mi. Will address that 1.5 mi in a separate project. Looking to coord with another project.
SRRTEP-W | 2018-01-08 | Ryan Dolan, AMP | Already know there will be another project? | AEP | Not sure.
SRRTEP-W | 2018-01-08 | Ed Tatum, AMP | As a process improvement , need to get the projects to the committee before they are under construction. | PJM | Understood. But things happen.
SRRTEP-W | 2018-01-08 | Ryan Dolan, AMP | Line retirement? See no issues. Have AEP or PJM studied? | AEP | A lot of develop potential in the area, ~200MW. Also, had a load shed issue in the area.
SRRTEP-W | 2018-01-08 | Mike Gahimer, IN Util Consumer Council | May not be needed immediately but is long term. So don't need to do this immediately, i.e., it does not need to be under construction at the time of the first read. | AEP | Performing inspections 8-10 yrs. Recent study identified serious deficiencies.
SRRTEP-W | 2018-01-08 | Ryan Dolan, AMP | Just rebuilt Poston-Hocking a few years ago. Why not rebuild at the same time? | AEP | Don't have info in front of them.
SRRTEP-W | 2018-01-08 | Ed Tatum, AMP | How many customers? | AEP | Serving one customer, Good Hope
SRRTEP-W | 2018-01-08 | Ryan Dolan, AMP | Consulted with customer before start work. | AEP | Not sure.
SRRTEP-W | 2018-01-08 | Bill Pazella, ODEC | 5 CB, How many to city? | AEP | split bus with tie breaker.
SRRTEP-W | 2018-01-30 | Ryan Dolan, AMP | Age of K2 CB | AEP | 1986
SRRTEP-W | 2018-01-30 | Ryan Dolan, AMP | Is CB fully depreciated? | AEP | Don' t have that info
SRRTEP-W | 2018-01-30 | Ryan Dolan, AMP | 3 sta serviced from this station? Is this the right location? | AEP | Yes. Yes.
SRRTEP-W | 2018-01-30 | Ryan Dolan, AMP | What is included in the cost? | AEP | Don't have all the details.
SRRTEP-W | 2018-01-30 | Ryan Dolan, AMP | How is DCIM allocated? | AEP | Should follow station, so distrib.
SRRTEP-W | 2018-01-30 | Ryan Dolan, AMP | Accounting of foundations? | AEP | steel is good.
SRRTEP-W | 2018-01-30 | Ryan Dolan, AMP | Age of Steel? | AEP | Don't have that info.
SRRTEP-W | 2018-01-30 | Ryan Dolan, AMP | Consulted with customer before start work. | AEP | Not sure.
SRRTEP-W | 2018-01-30 | Bill Pazella, ODEC | 5 CB, How many to city? | AEP | split bus with tie breaker.
SRRTEP-W | 2018-01-30 | Ryan Dolan, AMP | Age? | AEP | 1990. Need to confirm.
SRRTEP-W | 2018-01-30 | Ryan Dolan, AMP | Fault ops? | AEP | Don't have this info.
SRRTEP-W | 2018-01-30 | Ryan Dolan, AMP | Consider single circuit? | AEP | No, lots of taps.
SRRTEP-W | 2018-01-30 | Ryan Dolan, AMP | Could mitigate need for D/C? Consider | AEP | All part of the design considerations.
SRRTEP-W | 2018-01-30 | Bill Pazella, ODEC | Rebuilding only part of line. What about the remainder? | AEP | That portion was recently rebuilt. Matching rating.
SRRTEP-W | 2018-01-30 | Ryan Dolan, AMP | Why 138kV? | AEP | Not building new 46kV.
SRRTEP-W | 2018-01-30 | Ryan Dolan, AMP | Poss. To forgo Baileysville and Gyandotte and use existing? | AEP | Not sure.
SRRTEP-W | 2018-01-30 | Ryan Dolan, AMP | Is coal customer still there? | AEP | Suggesting adding 138-46 kV transformer at Gyandotte to same a bit of line?
SRRTEP-W | 2018-01-30 | Ryan Dolan, AMP | Number of MOABs on line? | AEP | 4 MOABs
SRRTEP-W | 2018-01-30 | Ryan Dolan, AMP | Can't tell if auto or manual from one-line? | AEP | Not the ones we have.
SRRTEP-W | 2018-01-30 | Ryan Dolan, AMP | Will a CB? | AEP | No
SRRTEP-W | 2018-01-30 | Ryan Dolan, AMP | No overlapping zones of protection? | AEP | No. That's the reason for the switcher.
SRRTEP-W | 2018-01-30 | Ryan Dolan, AMP | What happens to CB? | AEP | use as spare or parts.
SRRTEP-W | 2018-01-30 | Ryan Dolan, AMP | Why not wait on the breaker? | AEP | If do all this now, then So Bend is ready for 69kV conversion.
SRRTEP-W | 2018-01-30 | Ryan Dolan, AMP | Any redundant CB's that retiring? | AEP | Can't answer at that time.
SRRTEP-W | 2018-01-30 | Ryan Dolan, AMP | Wanted to bring back Sheridan? | AEP | Discussing on private call on Friday.
SRRTEP-W | 2018-02-14 | Ryan Dolan, AMP | Describe layout of straight bus. | ComEd | There is a bus CB that trips out whole station. Multiple lines.
SRRTEP-W | 2018-02-14 | Ryan Dolan, AMP | Looks like laying out for future? | ComEd | No room for breaker and half. Ring bus fit.
SRRTEP-W | 2018-02-14 | Ryan Dolan, AMP | CB on the Red bus between transformers | ComEd | circuit switcher, not CB
SRRTEP-W | 2018-02-14 | Ryan Dolan, AMP | Reuse existing CB? | ComEd | will eval material condition after removed.
SRRTEP-W | 2018-02-14 | Ryan Dolan, AMP | Provide additional info on how evaluate equip. | ComEd | Will ask specialist. Many criteria.
SRRTEP-W | 2018-02-14 | Ryan Dolan, AMP | Maintain or replace transformer? | ComEd | Maint in-service, some acoustics. Will watch.
SRRTEP-W | 2018-02-14 | Ryan Dolan, AMP | Replace transformer due to acoustics? | ComEd | Not per se, typ take a closer look.
SRRTEP-W | 2018-02-14 | Ryan Dolan, AMP | One Nelson outlet has add'l gens coming. ID issues in interconnection study? | ComEd | Ther e are wind and energy ctr projects. Not these. Interconnect on 345kV, this is 138kV
SRRTEP-W | 2018-02-14 | Ryan Dolan, AMP | How determine CB at EOL? | DUQ | These are the last 2 on the system. Historical issues and spare parts not available.
SRRTEP-W | 2018-02-14 | Ryan Dolan, AMP | Track number of CB failures? Willing to share? | DUQ | No.
SRRTEP-W | 2018-02-14 | Ryan Dolan, AMP | Any relaying costs? | DUQ | Just CB.
SRRTEP-W | 2018-02-14 | Ryan Dolan, AMP | If retire line, identified potential overloads? | AEP | Yes on other lines.
SRRTEP-W | 2018-02-14 | Ryan Dolan, AMP | Used PJM models? Cost to install line breakers? |  | Yes. Need to update.
SRRTEP-W | 2018-02-14 | Ryan Dolan, AMP | shared loads with PJM? Line reroute required? | AEP | Not at this time. Loads are pending. Yes, by state commission
SRRTEP-W | 2018-02-14 | Ryan Dolan, AMP | What was overloading? | AEP | Don't recall. Overloads were not the only reason the line was kept in service.
SRRTEP-W | 2018-02-14 | Bill Pazella, ODEC | Were all the lines the same size wire in the beginning? | AEP | Yes, 3/0 Cu
SRRTEP-W | 2018-02-14 | Bill Pazella, ODEC | Is that the largest conductor size? Enough head room? | AEP | Consider expected load growth?
SRRTEP-W | 2018-02-14 | Ryan Dolan, AMP | Do you have public documentation of the factors used to consider conductor size? | AEP | Cannot share info (NDA)
SRRTEP-W | 2018-02-14 | Ryan Dolan, AMP | What is your highest loading on facility?
SRRTEP-W | 2018-02-14 | Ryan Dolan, AMP | How does PJM accommodate bulk load additions? | PJM | Load forecast is based on know confirmed load. Additional load is a matter of scaling.
SRRTEP-W | 2018-02-14 | Ryan Dolan, AMP | Why only brought forward now.? | AEP | Immediate need. ID over-duty as part of interconnection study (end of 2017)
SRRTEP-W | 2018-02-14 | Ryan Dolan, AMP | When did construction start? Before overduty ID? | AEP | ok.
SRRTEP-W | 2018-02-14 | Ryan Dolan, AMP | Total number of P K breakers in system. | AEP | Don't have info
SRRTEP-W | 2018-02-14 | Ryan Dolan, AMP | Asked in December. Would appreciate the number. | AEP | of what value?
SRRTEP-W | 2018-02-14 | Ryan Dolan, AMP | Does AEP have a requirement to replace all PK breakers? | AEP | Yes.
SRRTEP-W | 2018-02-14 | Ryan Dolan, AMP | Why only see this now? | AEP | ID project. Slipped through the cracks. Field work initiated.
SRRTEP-W | 2018-02-14 | Ryan Dolan, AMP | What does "TW" mean? | AEP | Trapezoidal cable.
SRRTEP-W | 2018-02-14 | Ryan Dolan, AMP | Larger conductor? | AEP | See large load growth, will loop in another circuit to improve reliability.
SRRTEP-W | 2018-02-14 | Ryan Dolan, AMP | Upgrade to 138kV? | AEP | No.
SRRTEP-W | 2018-02-14 | Ryan Dolan, AMP | So field identified looping and conductor upsize? | AEP | No, Planning ID in design phase. Added those requirements.
SRRTEP-W | 2018-02-14 | Ryan Dolan, AMP | When will project start construction? | AEP | probably in the fall.
SRRTEP-W | 2018-02-14 | Ryan Dolan, AMP | Does Carbondale have 46kV at station? | AEP | Yes.
SRRTEP-W | 2018-02-14 | Ryan Dolan, AMP | Mammoth is in poor condition, doing work, why not build to Carbondale instead of Cabin Creek? | AEP | We think is the best soln.
SRRTEP-W | 2018-02-14 | Ryan Dolan, AMP | 15 mi of line from Clendenin, vs. 5 mi to Carbondale. Isn't it more cost effect? | AEP | Can look at, but don't believe that is cost effective.
SRRTEP-W | 2018-02-14 | Ryan Dolan, AMP | Follow up on other projects as well? | AEP | Yes.
SRRTEP-W | 2018-02-14 | Ryan Dolan, AMP | Anything to reduce the cost of the project? | AEP | Don't understand question?
SRRTEP-W | 2018-02-14 | Ryan Dolan, AMP | reduce conductor size? | AEP | minimal cost impact.
SRRTEP-W | 2018-02-14 | Ryan Dolan, AMP | How many overlap zones of protection after work? | AEP | None.
SRRTEP-W | 2018-02-14 | Ryan Dolan, AMP | How are bus and CTs protected? | AEP | will report back.
SRRTEP-W | 2018-02-14 | Ryan Dolan, AMP | Severe condition issues with towers. | AEP | Lattice towers. More difficult to assess. Field visit and ID condition is worse.
SRRTEP-W | 2018-02-14 | Ryan Dolan, AMP | Provide photo doc of condition. | AEP | Not providing level of detail.
SRRTEP-W | 2018-02-14 | Ryan Dolan, AMP | Didn't see the line condition you describe. | AEP | Report from professional engineers. Not providing that level of detail.
SRRTEP-W | 2018-02-14 | Ryan Dolan, AMP | Stakeholders don't need that info? | AEP | Comply with understanding of direction from FERC.
SRRTEP-W | 2018-02-14 | Ryan Dolan, AMP | Potential alternatives last time. Any review? | AEP | Actually was the other side of the line.
SRRTEP-W | 2018-02-14 | Ryan Dolan, AMP | Alternatives for this. Considered? Keep this line and retire other. | AEP | Not think its viable.
SRRTEP-W | 2018-02-14 | Ryan Dolan, AMP | Why not using 3 winding transformer | AEP
SRRTEP-W | 2018-02-14 | Ryan Dolan, AMP | in this area 34kV is distribution? So split costs? | AEP | This is all booked as transmission. The state does not allow split accounting.
SRRTEP-W | 2018-02-14 | Ryan Dolan, AMP | Will transco own any of these assets? | AEP | No.
SRRTEP-W | 2018-02-14 | Ryan Dolan, AMP | What could decrease the cost of the project? | AEP
SRRTEP-W | 2018-02-14 | Ryan Dolan, AMP | Anything that could reduce the cost? Perhaps 138/69/12kV transformer? | AEP | We think the project is cost effective. moving distrib off transformer. Using 138/12 kV transformer too.
SRRTEP-W | 2018-02-14 | Ryan Dolan, AMP | transformer at New Philly is t or D? model info. Using FERC 715 criteria. | AEP | Distribution. No, not a FERC 715 criteria.
SRRTEP-W | 2018-02-14 | Bill Pazella, ODEC | Upgrade to larger conductor? | AEP | Near load center so increased?
SRRTEP-W | 2018-02-14 | Ryan Dolan, AMP | Evaluate line into Ruth? | AEP | Makes no sense to eliminate a feed into Charleston.
SRRTEP-W | 2018-02-14 | Ryan Dolan, AMP | Hill is Distr? | AEP | Transmission
SRRTEP-W | 2018-02-14 | Ryan Dolan, AMP | Is the station T or D? | AEP | It is a T load, but part of the load is distrib.
SRRTEP-W | 2018-02-14 | Ryan Dolan, AMP | Is it a T or D station? | AEP/PJM | The station cost is $0 so should be Distrib. The line cost only is T. / Also note that the prior conversation was related to WV and this project is in VA.
SRRTEP-W | 2018-02-14 | Ryan Dolan, AMP | What state? What are the accounting practices? | AEP | KY. Not sure
SRRTEP-W | 2018-02-14 | Ryan Dolan, AMP | Distrib is paying for a majority of the work? | AEP | Yes.
SRRTEP-W | 2018-02-14 | Ryan Dolan, AMP | Why so late? | AEP | Distrib sponsor. A little late getting started.
SRRTEP-W | 2018-02-14 | Ryan Dolan, AMP | What is being done with the extra CB? | AEP | Converting SF6 CB to 69kV CB.
SRRTEP-W | 2018-02-14 | Ryan Dolan, AMP | How old? | AEP | 1968 vintage.
SRRTEP-W | 2018-02-14 | Ryan Dolan, AMP | How much will that reduce the load? | ATSI | <missed answer
SRRTEP-W | 2018-02-14 | Ryan Dolan, AMP | How will this break up the customers? Overall condition of line? | AEP | Can look into.
SRRTEP-W | 2018-02-14 | Ryan Dolan, AMP | Looking for customer redistrib, etc. | ATSI
SRRTEP-W | 2018-02-14 | Ryan Dolan, AMP | CB on high side? Same on Distrib side? | ATSI | yes. Distrib makes the decision on distrib scope.
SRRTEP-W | 2018-02-14 | Ryan Dolan, AMP | Are we isolating from D failures? | ATSI | Can't answer that.
SRRTEP-W | 2018-02-14 | Ryan Dolan, AMP | Use switcher or only CB? | ATSI | both. Or fuses
SRRTEP-W | 2018-02-14 | Ryan Dolan, AMP | Considered circuit sw?
SRRTEP-W | 2018-02-14 | Ryan Dolan, AMP | Same questions as last time. How much risk exposure remains.
SRRTEP-W | 2018-02-14 | Ryan Dolan, AMP | Are these projects still in conceptual? | AEP | Some may shift.
SRRTEP-W | 2018-02-14 | Ryan Dolan, AMP | Update slide?
SRRTEP-W | 2018-02-14 | Ryan Dolan, AMP | One of your larger projects? | ATSI | geographically.
SRRTEP-W | 2018-02-14 | Ryan Dolan, AMP | Are there taps we are not seeing? | ATSI | 7 taps on the line.
SRRTEP-W | 2018-02-14 | Ryan Dolan, AMP | Can you show the other taps? | ATSI | Many got covered up.
SRRTEP-W | 2018-02-14 | Ryan Dolan, AMP | Load drop?
SRRTEP-W | 2018-02-14 | Ryan Dolan, AMP | Conductor sizing issues?
SRRTEP-W | 2018-02-14 | Ryan Dolan, AMP | Driver? | ATSI | Many issues. 300 rejected poles. Mixed conductor. Many others.
SRRTEP-W | 2018-02-14 | Ryan Dolan, AMP | to provide detailed info of all conditions | ATSI | will consider.
SRRTEP-W | 2018-03-09 | Ryan Dolan, AMP | Which circuit tapping? | RMU | in the Glidden-DeKalb circuit.
SRRTEP-W | 2018-03-09 | Ryan Dolan, AMP | any sectionalizing required at Twombley? | RMU | not determined yet.
SRRTEP-W | 2018-03-09 | Ryan Dolan, AMP | Existing ring bus? | RMU | Yes. Adding one CB, poss. 2 CB
SRRTEP-W | 2018-03-09 | Ryan Dolan, AMP | Consider right in DeKalb? | RMU | No transmission CB, only circuit switcher. Line tap allows protect at Glidden station.
SRRTEP-W | 2018-03-09 | Ryan Dolan, AMP | Conductor size? RMU using 556? | RMU | in discussion with ComEd, did 10xx. Yes other lines are 556?
SRRTEP-W | 2018-03-09 | Ryan Dolan, AMP | Any protection changes | PJM | No significant change.
SRRTEP-W | 2018-03-09 | Ryan Dolan, AMP | See three projects in the area plus existing deficiency. Could these have been consolidated together? | RMU | Can only speak to RMU project.
SRRTEP-W | 2018-03-09 | Ryan Dolan, AMP | What is "development" | DEOK | Scoping.
SRRTEP-W | 2018-03-09 | Ryan Dolan, AMP | Closest breaker? | AEP | Not sure.
SRRTEP-W | 2018-03-09 | Ryan Dolan, AMP | Who will owe the CB? | AEP | How is ownership relevant?
SRRTEP-W | 2018-03-09 | Ryan Dolan, AMP | Line is owed by Transource? | AEP | Transource is an AEP company. Control of the through path is one and the same
SRRTEP-W | 2018-03-09 | Ryan Dolan, AMP | This changes the interconnection agreement? | AEP/PJM | Not sure. Have to look into./ Will look into it.
SRRTEP-W | 2018-03-09 | Ryan Dolan, AMP | What conductor exsting and planned | DEOK | several existing. Final decision not made.
SRRTEP-W | 2018-03-09 | Ryan Dolan, AMP | Highest loading? | DEOK | Don't have
SRRTEP-W | 2018-03-09 | Ryan Dolan, AMP | Did "do no harm" analysis? | PJM | Yes
SRRTEP-W | 2018-03-09 | Ryan Dolan, AMP | Would lower loading be ok? | PJM | No issues at 114MVA.
SRRTEP-W | 2018-03-09 | Ryan Dolan, AMP | Require conductor size on baseline, supplemental? | PJM | No. For competitive, PJM requires for independent cost estimate
SRRTEP-W | 2018-03-09 | Ryan Dolan, AMP | Why supplemental and not baseline? | AEP/PJM | Driver is an other supplemental project./ slide is incorrect. This is a supplemental project. Supplemental causes a reliability violation. Supplemental is required to address.
SRRTEP-W | 2018-03-09 | Ryan Dolan, AMP | Driver is the Sheridan station upgrade. | PJM | We missed. Catching up now.
SRRTEP-W | 2018-03-09 | Ryan Dolan, AMP | Doing anything on high side of distrib transformer? | AEP | Yes. Don't want faults on D to impact T.
SRRTEP-W | 2018-03-09 | Ryan Dolan, AMP | Will you respond to posted questions? | AEP | Working on it. Will update slides as appropriate.
SRRTEP-W | 2018-03-09 | Ryan Dolan, AMP | Why using non-std trap wire? | AEP | Is a std and
SRRTEP-W | 2018-03-09 | Ryan Dolan, AMP | What is cost diff in using more std wire? | AEP | Will have to follow up.
SRRTEP-W | 2018-03-09 | Ryan Dolan, AMP | How justify change in conductor? | AEP | Can't say. Engineering thought it was the appropriate solution?
SRRTEP-W | 2018-03-09 | Ryan Dolan, AMP | Want this project to come back again until the answers are given. | PJM | Working on it.
SRRTEP-W | 2018-03-09 | Ryan Dolan, AMP | Totally appropriate to ask if this design is cost effective. | AEP/Buckeye | Potentially looping in a 138kV line and upgrade to 138kV. Will come back with the cost difference. Regarding loading. Line operated open. Closing overloads. Coops were effectively fed radilally. Have been asking AEP to rebuild line for quite a while.
SRRTEP-W | 2018-03-09 | Ryan Dolan, AMP | What is the load increase? | DEOK | For mode used 10mVA.
SRRTEP-W | 2018-03-09 | Ryan Dolan, AMP | What load increase was presented. | PJM | Not sure.
SRRTEP-W | 2018-03-09 | Ryan Dolan, AMP | List of PCLRWs? | AEP | Would have to go back.
SRRTEP-W | 2018-03-09 | Ryan Dolan, AMP | Wonder if same as the conting. Any recent block loads? | AEP | Yes, there have been. How is this relevant?
SRRTEP-W | 2018-03-09 | Ryan Dolan, AMP | Is it a supplement block load driving a baseline project. | AEP | all of the issues are driving the baseline. AEP is taking advantage of the work to do some supplemental work.
SRRTEP-W | 2018-03-09 | Ryan Dolan, AMP | Conductor size? | DEOK | Don't know
SRRTEP-W | 2018-03-09 | Ryan Dolan, AMP | Limiting element?
SRRTEP-W | 2018-03-09 | Ryan Dolan, AMP | Potential to upgrade? | AEP/Buckeye | Can't say./ Petersburg is our number 1 source of outages. Very motived to get it done.
SRRTEP-W | 2018-03-09 | Ryan Dolan, AMP | Windings on transformer?
SRRTEP-W | 2018-03-09 | Ryan Dolan, AMP | Do you look into alternatives suggested? | AEP | Yes. Lots of coal in the area, i.e., customers. No customers in the proposed route. We are giving you primary and secondary lines. And we are debating secondary regions.
SRRTEP-W | 2018-03-09 | Ryan Dolan, AMP | age of CB K | AEP | 1996
SRRTEP-W | 2018-03-09 | Ryan Dolan, AMP | Depreciation schedule? | AEP | known issues with these CBs. Depreciation not a factor.
SRRTEP-W | 2018-03-09 | Ryan Dolan, AMP | Why not go back wint 90MVA transformer? | AEP | Not sure. But not something that typically put on system.
SRRTEP-W | 2018-03-09 | Ryan Dolan, AMP | Recent baseline at this station? | AEP | There was a project 4 yrs ago. 2 zones of protection, not 3
SRRTEP-W | 2018-03-09 | Ryan Dolan, AMP | 69/4 kV, says 138kV on slide | AEP | Actually, it is 138kV
SRRTEP-W | 2018-03-09 | Ryan Dolan, AMP | Was a high cap S/C considered? | AEP | No. No vehicle to do a retirement study.
SRRTEP-W | 2018-03-09 | Ryan Dolan, AMP | No but you can do a topo modi eval? | AEP | Yes, but not mechanism to eval retiring a line. There are loads tapped each side of line.
SRRTEP-W | 2018-03-09 | Ryan Dolan, AMP | What work being done at East Elkhart? | AEP | Stations on 34.5kV line. Not direct.
SRRTEP-W | 2018-03-09 | Ryan Dolan, AMP | 69kV in the area? | AEP | Plan is to upgrade 34.5 to 69kV.
SRRTEP-W | 2018-03-09 | Ryan Dolan, AMP | Wood or steel? Was wood considered? | AEP | Steel. Can follow u p, but not sure.
SRRTEP-W | 2018-03-09 | Ryan Dolan, AMP | For full rebuild, didn't really look at wood? | AEP | Correct.
SRRTEP-W | 2018-03-09 | Ryan Dolan, AMP | 336 or 565 considered? Please try to make the plan clearer. Looks like a double circuit. | AEP | 336 no. 565 was. But other work in the area, so sized for that future path. Will work on that.
SRRTEP-W | 2018-03-09 | Ryan Dolan, AMP | Designed fo 138kV? | AEP | No. numerous customers who would not want to upgrade.
SRRTEP-W | 2018-03-09 | Ryan Dolan, AMP | Existing conductor? | AEP | On slide.
SRRTEP-W | 2018-03-09 | Ryan Dolan, AMP | 138/34.5kV T or D asset? | AEP | Trans. It depends on how the asset was booked. If you have issues with the accounting, take up in another forum.
SRRTEP-W | 2018-03-09 | Ryan Dolan, AMP | PJM reviiew. | PJM/AEP | No justification./ FERC issue. Accounting follows FERC guidance.
SRRTEP-W | 2018-03-09 | Ryan Dolan, AMP | Why not 138kV design? | AEP | 69kV at each end. Not reason to upgrade.
SRRTEP-W | 2018-03-09 | Ryan Dolan, AMP | there are two large 138kV networks east and west of here. No need to upgrade? | AEP | No.
SRRTEP-W | 2018-03-09 | Ryan Dolan, AMP | All stations being converted, who pays? | AEP | AEP but also load.
SRRTEP-W | 2018-03-09 | Ryan Dolan, AMP | transformer cost? | AEP | transformer is distr. The costs only incl. T cost.
SRRTEP-W | 2018-03-09 | Ryan Dolan, AMP | Rebuilding as D/C? | AEP | No. Building parallel to existing 138kV
SRRTEP-W | 2018-03-09 | Ryan Dolan, AMP | 138/34 is distribution? | AEP | Yes. AEP-Ohio considers 34kV as distribution.
SRRTEP-W | 2018-03-09 | Ryan Dolan, AMP | D station? So everything is D? | AEP | Yes. Only showing T cost. Following FERC rules. Varies by state. If need more info, will set up meeting with finance.
SRRTEP-W | 2018-03-09 | Ryan Dolan, AMP | AMP customer with CB at Station. Any impacts? | AEP | No impact.
SRRTEP-W | 2018-03-09 | Ryan Dolan, AMP | Who pays for metering? | AEP | Coal customer pays upgrade. Metering cost is distrib. Slide is correct.
SRRTEP-W | 2018-03-09 | Ryan Dolan, AMP | In Ohio 34kV is distrib? | AEP | In some areas T, some in D
SRRTEP-W | 2018-03-09 | Ryan Dolan, AMP | How handle smart grid load shift? | AEP | This is the way the asset is booked, not really appropriate forum?
SRRTEP-W | 2018-03-09 | Ryan Dolan, AMP | What if loop a 34kV line, will it become a T asset? | AEP | Can't speculate. It really depends on what are trying accomplish.
SRRTEP-W | 2018-03-09 | Ryan Dolan, AMP | Alternatives to D/C? | AEP | it is very congested. I must d/c with an existing circuit near Zanesville
SRRTEP-W | 2018-03-09 | Ryan Dolan, AMP | Estimate for alternate? | AEP | still with estimating
SRRTEP-W | 2018-03-09 | Ryan Dolan, AMP | What about the 138/69 alt. | AEP | $25M
SRRTEP-W | 2018-03-09 | Ryan Dolan, AMP | Cost with additional upgrade, is it less than the proposed? | AEP | Need two sources into Mt. Sterling. Need to also do one of the line builds.
SRRTEP-W | 2018-03-09 | Ryan Dolan, AMP | Standard for re-routed lines? | AEP | Not sure will need to follow up
SRRTEP-W | 2018-03-09 | Ryan Dolan, AMP | Why 138kV? | AEP | Plans to rebuild to 138kV. Many parts already built to 138kV
SRRTEP-W | 2018-03-09 | Ryan Dolan, AMP | 69kV switch? | AEP | Yes.
SRRTEP-W | 2018-03-09 | Ryan Dolan, AMP | cost is just to reinforce? | AEP | Yes.
SRRTEP-W | 2018-03-09 | Ryan Dolan, AMP | Which customers feed from Somerset | AEP | That radial is owned by the customer. Somerset sw feeds the coop. Zionsville sw feeds to trans.
SRRTEP-W | 2018-03-09 | Ryan Dolan, AMP | toto 69kV exits at Somerset? | AEP | 4
SRRTEP-W | 2018-03-09 | Ryan Dolan, AMP | When expect to rebuild orig Vick-Schoolcraft line? | AEP | Need to do this work first. Will then re-eval.
SRRTEP-W | 2018-03-09 | Ryan Dolan, AMP | Why not build d/c now and retire existing? | AEP | Some additional cost. Don't have a complete answer. (Kameron) This is a new line, new row. This is a not interruptible load, need a separate path.
SRRTEP-W | 2018-03-09 | Ryan Dolan, AMP | Why not do nothing? | ComEd | Because single breaker takes out the whole station.
SRRTEP-W | 2018-03-27 | Ryan Dolan, AMP | Still in scoping.? | AEP | It was at the time. Probably in engineering.
SRRTEP-W | 2018-03-27 | Ryan Dolan, AMP | Baseline? | AEP/PJM | 96% of loading. Not a baseline./ Did not check if there are PCLRW's open on the line.
SRRTEP-W | 2018-03-27 | Ryan Dolan, AMP | What model do we need to look at verify? | AEP | Need ops model but do not publish. can provide screenshot of SCADA data.
SRRTEP-W | 2018-03-27 | Ryan Dolan, AMP | Consider looping in other lines and retiring? Is this an issue that caused other outages in the area. | DEOK | no. This is 4/0 Cu on limiting a 138kV. So it seems pretty clear.
SRRTEP-W | 2018-03-27 | Ryan Dolan, AMP | Driver? | DUQ | Relocating substation to add more D feeders (urban area, land
SRRTEP-W | 2018-03-27 | Ryan Dolan, AMP | # of CB? Ratings? Fault duty of CB? | DUQ | 4 138kV CB. 3kA CB. Don't have.
SRRTEP-W | 2018-03-27 | Ryan Dolan, AMP | How much of the alternative cost would have been T? | AEP | That is somewhat dependent on where the load was transferred?
SRRTEP-W | 2018-03-27 | Ryan Dolan, AMP | Is the customer paying? Seems like the costs are due to customer? | AEP | AEP Ohio station being relocated. Also a load increase. The load increase is the driver. This is the most cost effective solution.
SRRTEP-W | 2018-03-27 | Ryan Dolan, AMP | Is the relocation due to space requirements, or the customer expansion? | AEP | The customer is expanding, they are expanding into their own space that could have been used to expand the station.
SRRTEP-W | 2018-03-27 | Ryan Dolan, AMP | What bkr would operate for the on the 138kV. | AEP | Nine brk & 1/2 strings, so on a bus fault, 9 brks open. Adding tie bkr
SRRTEP-W | 2018-03-27 | Ryan Dolan, AMP | Some bkrs operate open? | AEP | This is will be changed in a project presented at TEAC
SRRTEP-W | 2018-03-27 | Ryan Dolan, AMP | what is the limit on the "6"? | AEP | has to due with the relay interface module. Standard interface has 6 positions.
SRRTEP-W | 2018-03-27 | Ryan Dolan, AMP | Does/did this station have short circuit issues? | AEP | it did, but is reduced due to gen retirements.
SRRTEP-W | 2018-03-27 | Ryan Dolan, AMP | Are the series reactors in the other project still needed? | AEP | Yes.
SRRTEP-W | 2018-03-27 | Ryan Dolan, AMP | Justif bus tie breaker? | AEP | Bus fault drops all 4 transformers
SRRTEP-W | 2018-03-27 | Ryan Dolan, AMP | All serve load? Std for when need bus tie? | AEP | Not sure. Not sure there is a written standard. for breaker & half, no more than 6 elements.
SRRTEP-W | 2018-03-27 | Ryan Dolan, AMP | Do you also study impact on FE system? | AEP | Yes.
SRRTEP-W | 2018-03-27 | Ryan Dolan, AMP | PJM analysis completed? | PJM | No.
SRRTEP-W | 2018-03-27 | Ryan Dolan, AMP | Does this eliminate need to previously approved projects? | PJM | We are looking but there are limits as to what we can review.
SRRTEP-W | 2018-03-27 | Ryan Dolan, AMP | Customer is installing? | AEP | Will have to follow up
SRRTEP-W | 2018-03-27 | Ryan Dolan, AMP | Plans to loop in radial? | AEP | Looking into but given pace of project, not feasible now.
SRRTEP-W | 2018-03-27 | Ryan Dolan, AMP | Upgrading to 69kV? | AEP | yes.
SRRTEP-W | 2018-03-27 | Ryan Dolan, AMP | Any alternatives considered? | AEP | Yes, overlooked that slide.
SRRTEP-W | 2018-03-27 | Ryan Dolan, AMP | Consider upgrade Elkhart Hydro-Dunlap? Why build 69kV? | AEP | Not sure? Operated at 34kV but all system in area built to 69kV. No driver yet.
SRRTEP-W | 2018-03-27 | Ryan Dolan, AMP | 69/12kV transformer. T cost? And the 12kV breakers? | AEP | Distribution. Yes.
SRRTEP-W | 2018-03-27 | Ryan Dolan, AMP | reflected in cost estimates? | AEP | Yes. Only T cost shown
SRRTEP-W | 2018-03-27 | Ryan Dolan, AMP | Land cost is D? Any alt. address 3 way switch? We can anticipate a future proj? | AEP | 3 lines coming together, so it a T station. The lower voltage assets should be dist. No. Yes.
SRRTEP-W | 2018-03-27 | Ryan Dolan, AMP | Add'l load and growth in the area? No other stations not shown on map? | AEP | Will confirm the cost breakdown. No. No.
SRRTEP-W | 2018-03-27 | Ryan Dolan, AMP | Driver was an overload of the facility? | PJM | Ready a relocation to accommodate previously approved project.
SRRTEP-W | 2018-03-27 | Ryan Dolan, AMP | Circuit switch on the high side? | AEP | yes. Did not appear cost effective. A lot of bus work.
SRRTEP-W | 2018-03-27 | Ryan Dolan, AMP | Decision to go into DeKalb, considered wind gen going in nearby? | RMU | Don't see any impact of wind projects
SRRTEP-W | 2018-03-27 | Ryan Dolan, AMP | Was a transposer consider? Or two? | AEP | Can look into that.
SRRTEP-W | 2018-03-27 | Ryan Dolan, AMP | Assoc of any baseline project in the area? | AEP | Not that I am aware of.
SRRTEP-W | 2018-03-27 | Ryan Dolan, AMP | Replacing all oil CB? | AEP | Yes. Have addressed this before.
SRRTEP-W | 2018-03-27 | Ryan Dolan, AMP | Fault ratings, ops? | AEP | Thought they were on the slides. We will get back to you.
SRRTEP-W | 2018-03-27 | Ryan Dolan, AMP | Installing DICM? Any high side 69kV work? | AEP | DICM is distrib cost. Relay upgrades are T cost.
SRRTEP-W | 2018-03-27 | Ryan Dolan, AMP | Why no tie breaker? | DEOK/AEP | No./ Space constraints.
SRRTEP-W | 2018-03-27 | Ryan Dolan, AMP | Would you do this work if D wasn't working there? | AEP | It was on the aging equip list. But timing made sense.
SRRTEP-W | 2018-03-27 | Ryan Dolan, AMP | What conductor size? | DEOK | Not sure. Will exceed the rating of the bus.
SRRTEP-W | 2018-03-27 | Ryan Dolan, AMP | Asked last time | DEOK | Still scoping so conductor not yet selected.
SRRTEP-W | 2018-03-27 | Ryan Dolan, AMP | In/out or hard tap? Where outages with a particular customer? | DEOK/AEP | Probably in/out. 3 loads. Steel, hospital, GE.
SRRTEP-W | 2018-03-27 | Ryan Dolan, AMP | So just make all the costs D? Other loads are networks. Only radial load is Steel. Project is almost x2 the cost. | AEP/DEOK | Did talk with customer. They were unwilling to take outages. Depends on how the asset is booked.
SRRTEP-W | 2018-03-27 | Ryan Dolan, AMP | Standard methodology? | AEP/DEOK | Steel customer typically max. 8 hr window. will get the details and get back to you./ Don't know. Question for finance.
SRRTEP-W | 2018-03-27 | Ryan Dolan, AMP | Are these pole top structures? | DEOK | This is just an artifact of the mapping. Shows lines & poles
SRRTEP-W | 2018-03-27 | Ryan Dolan, AMP | conductor size? | DEOK | Not sure.
SRRTEP-W | 2018-03-27 | Ryan Dolan, AMP | What is the next limtiing element? | DEOK | Not sure. Would have to look in DB.
SRRTEP-W | 2018-03-27 | Ryan Dolan, AMP | Like Sunbright. Why no T cost? | AEP | No T cost on Sunbright
SRRTEP-W | 2018-03-27 | Ryan Dolan, AMP | Program to replace oil-filled breakers? | DEOK | Not as such. As touch stations, try to clean up other devices, e.g., oil breakers
SRRTEP-W | 2018-03-27 | Ryan Dolan, AMP | Where pick up load? | AEP | Keep line in service, so not loss of load. No new load. Just diversifying. D is building a new station. Easier to add CB there.
SRRTEP-W | 2018-03-27 | Ryan Dolan, AMP | Don't challenge the need for the load? Systematic way to determine line replacements? | AEP | That's not our obligation. That is a state regulatory issue.
SRRTEP-W | 2018-03-27 | Ryan Dolan, AMP | So no limit on service that D can ask for? | DEOK | No written, public standard.
SRRTEP-W | 2018-03-27 | Ryan Dolan, AMP | Internal doc? | AEP/DEOK | there is a limit. But all customers have same access./ Can't say. Part of asset mgmt.
SRRTEP-W | 2018-03-27 | Ryan Dolan, AMP | All equipment to 69kV? | AEP | No, only serving IMPA. So only 34kV.
SRRTEP-W | 2018-03-27 | Ryan Dolan, AMP | 69kV bkr? | AEP | Yes.
SRRTEP-W | 2018-03-27 | Ryan Dolan, AMP | Manufacturer of CB? | AEP | ITE.
SRRTEP-W | 2018-03-27 | Ryan Dolan, AMP | D or T? | AEP | T station, with D assets.
SRRTEP-W | 2018-03-27 | Ryan Dolan, AMP | DCIM is D cost? | AEP | Yes.
SRRTEP-W | 2018-03-27 | Ryan Dolan, AMP | removal of transformer is T cost? | AEP | Yes, booked as T.
SRRTEP-W | 2018-03-27 | Ryan Dolan, AMP | Only 1 transformer? | AEP | Yes.
SRRTEP-W | 2018-03-27 | Ryan Dolan, AMP | Thanks for getting to one of AMPS' | AEP | 161/34.5kV station, AEP
SRRTEP-W | 2018-03-27 | Ryan Dolan, AMP | consider change to 138kV? | AEP | TVA tie lin. TVA not interested changing?
SRRTEP-W | 2018-03-27 | Ryan Dolan, AMP | When design for 5 transformer, install all 5? | AEP | No just 1 for now. Room for growth.
SRRTEP-W | 2018-03-27 | Ryan Dolan, AMP | bus config? | AEP | Ultimately, a ring bus but for now only 2 CB, either side of transformer.
SRRTEP-W | 2018-03-27 | Ryan Dolan, AMP | Line is in/out? | AEP
SRRTEP-W | 2018-03-27 | Ryan Dolan, AMP | Poss. To just build Grandview to Bendix | AEP | Can look at it.
SRRTEP-W | 2018-03-27 | Ryan Dolan, AMP | New line exit for | AEP | toward Roanoke.
SRRTEP-W | 2018-03-27 | Ryan Dolan, AMP | Any work on the line with Reusen? | AEP | CB A being replaced.
SRRTEP-W | 2018-03-27 | Ryan Dolan, AMP | AMP customer on A. Still exposed to line outages. | AEP | Please send concerns. So we can understand your exposure.
SRRTEP-W | 2018-03-27 | Ryan Dolan, AMP | If drop transformer , AMP exposed to line outages. | AEP | will look into. Cap bank and ?? Will be attached off the bus, not off the line.
SRRTEP-W | 2018-03-27 | Ryan Dolan, AMP | how run RTEP, i.e., how ensure that no supplementals don't impact reliability? | PJM | Will study and react. If an existing projects can be expanded to address the issue. Sure.
SRRTEP-W | 2018-03-27 | Ryan Dolan, AMP | Both lines there today? | AEP | There is one line there today. Green is existing. Red is the reroute.
SRRTEP-W | 2018-03-27 | Ryan Dolan, AMP | 138 project in the area. | AEP | haviland, East Lime ties in as well.
SRRTEP-W | 2018-03-27 | Ryan Dolan, AMP | how run RTEP, i.e., how ensure that no supplementals don't impact reliability? | PJM | Will study and react. If an existing projects can be expanded to address the issue. Sure.
SRRTEP-W | 2018-04-17 | Ryan Dolan, AMP | will be providing a standard list of questions shortly after meeting. | PJM | Thank you.
SRRTEP-W | 2018-04-17 | Bill Pazella, ODEC | If cut in new customer, making it a 3 breaker ring bus? | AEP | Also, a distrib transformer,
SRRTEP-W | 2018-04-17 | Ryan Dolan, AMP | Distance from Bryce to Refugee Rd?
SRRTEP-W | 2018-04-17 | Ryan Dolan, AMP | New circ adjacent to existing | AEP | Don't know. Haven't located station yet.
SRRTEP-W | 2018-04-17 | Ryan Dolan, AMP | consider D/c? Would MOABs work? | AEP | Yes, makes sense in the future but not now. Asking not to allow momentary outages.
SRRTEP-W | 2018-04-17 | Ryan Dolan, AMP | Should have a long term plan in place. If access to park land may drive a d/c. | PJM | Stopped conversation. Take offline
SRRTEP-W | 2018-04-17 | Ryan Dolan, AMP | transformer section schem. Is there sep or transformer? Possible to eliminate transformer | AEP | Mix of transformers. There is separation, different uses. Not sure that it is possible. Can get details for you.
SRRTEP-W | 2018-04-17 | Ryan Dolan, AMP | Replace CB 2 (Q) at Linchburg | AEP | Error, should be CB C
SRRTEP-W | 2018-04-17 | Ryan Dolan, AMP | CB age? Why not just maintenance? | AEP | Don't have info. Will need to follow up
SRRTEP-W | 2018-04-17 | Ryan Dolan, AMP | What are the "A" and the "B" conditions? | AEP | Don't have the complete list in front of me.
SRRTEP-W | 2018-04-17 | Ryan Dolan, AMP | Decide to convert to 138kV? | AEP | Initially, don't have 138kV source in the area. But another project will provide 138kV.
SRRTEP-W | 2018-04-17 | Ryan Dolan, AMP | Can you build to 69kV and support the load? | AEP | Operational flexibility drives desire to build to 138kV.
SRRTEP-W | 2018-04-17 | Ryan Dolan, AMP | Cost of alternative? | AEP | About $300K less. For 69kV
SRRTEP-W | 2018-04-17 | Ryan Dolan, AMP | Would do this without distrib driver? | AEP | Driver is still valid. Coord work with AEP Ohio. Trying to do work efficiently. Schedule would be about the same.
SRRTEP-W | 2018-04-17 | Ryan Dolan, AMP | Consider two switches in series? | AEP | Yes. Space constrained. This is a more attractive solution.
SRRTEP-W | 2018-04-17 | Ryan Dolan, AMP | transformer is part of ring bus, so transformer failure takes out all load? | AEP | Yes.
SRRTEP-W | 2018-04-17 | Ryan Dolan, AMP | Submitted to VA commission yet? | AEP | Don't have that info. Don't know if it is required. Will follow up
SRRTEP-W | 2018-04-17 | Ryan Dolan, AMP | Does the alt. cost include the D costs? | AEP | yes. Deduct $6.6M from that as well.
SRRTEP-W | 2018-04-17 | Bill Pazella, ODEC | replace S/C with D/C? | AEP | replacing two S/C with a D/C line up to Clinton. S/C after than. For one circ, ownership of line changes to DPL(?)
SRRTEP-W | 2018-04-17 | Bill Pazella, ODEC | Use MOAB for sectionalizing? | AEP | Yes.
SRRTEP-W | 2018-04-17 | Ryan Dolan, AMP | Any circ operated as N.O.? | AEP | Yes, for AEP.
SRRTEP-W | 2018-04-17 | Ryan Dolan, AMP | DPL has same issue? | AEP | Cannot say. DPL needs to address. We are coordinating.
SRRTEP-W | 2018-04-17 | Ryan Dolan, AMP | Have you looked at combining? | AEP | Not eliminating a circuit. Eliminating a pole line. No no harm flags. So no reliability impact. Have not studied retirement of a line.
SRRTEP-W | 2018-04-17 | Ryan Dolan, AMP | Does MPOI justify install of CB? | AEP | Will follow up on calcs? Think is was more to reduce line exposure.
SRRTEP-W | 2018-04-17 | Bill Pazella, ODEC | Consider 138kV? transformer paid for by whom? | AEP | No sources in the area and 6 customer subs to upgrade. So not ideal. Customer.
SRRTEP-W | 2018-04-17 | Bill Pazella, ODEC | Is there a threshold for T-line cut in? | AEP | Distr tap was looked at. T-line cutin was more cost effective.
SRRTEP-W | 2018-04-17 | Ryan Dolan, AMP | Why no T-costs? Eliminated the limiting element on line? | AEP | D sub. All costs to Distrib. Not sure, but will follow up
SRRTEP-W | 2018-04-17 | Ryan Dolan, AMP | Circuit rating? | AEP | Not sure. Will follow up
SRRTEP-W | 2018-04-17 | PJM Customer Advocates | This is a T cost? | AEP | Yes.
SRRTEP-W | 2018-04-17 | Ryan Dolan, AMP | What station is the min. lost? | AEP | Not sure. Interrupts a big customer.
SRRTEP-W | 2018-04-17 | Ryan Dolan, AMP | Part of the issue is line lengths? | AEP | The customer feels that a closer tap will help reliability.
SRRTEP-W | 2018-04-17 | Ryan Dolan, AMP | Driver? | AEP | Should have stated that distrib is driver, not just T planning.
SRRTEP-W | 2018-04-17 | Ryan Dolan, AMP | Is this new load? | AEP | Believe it is just redistribution of existing load.
SRRTEP-W | 2018-04-17 | Ryan Dolan, AMP | Resilience, is that is a new category? | AEP | Would consider it more op. flexiblity. Will change back to be consistent
SRRTEP-W | 2018-04-17 | Ryan Dolan, AMP | transformer not included? | AEP | Cost updated to include.
SRRTEP-W | 2018-04-17 | Ryan Dolan, AMP | Why remove CB E? | AEP | Not needed. Is a bus tie breaker. Consolidate onto a single bus.
SRRTEP-W | 2018-04-17 | Ryan Dolan, AMP | How did you do that study? | AEP | No real study. Recognized no longer needed.
SRRTEP-W | 2018-04-17 | Ryan Dolan, AMP | Any stations needing renewal in the area? | AEP | Annual review. May come up again in the area. Should not in this area.
SRRTEP-W | 2018-04-17 | Ryan Dolan, AMP | Any other projects in the area? | AEP | Yes, Sardinai. Some of line will be retired.
SRRTEP-W | 2018-04-17 | Ryan Dolan, AMP | Did look a try to optimize projects? | AEP | Yes.
SRRTEP-W | 2018-04-17 | Ryan Dolan, AMP | considered retiring line? | AEP | Yes. Not desireable
SRRTEP-W | 2018-04-17 | Ryan Dolan, AMP | Retire CB at Bannock? What is the driver? Reroute? | AEP | Yes. Not sure why. Will need to follow-up. National forest. Limited ability.
SRRTEP-W | 2018-04-17 | Ryan Dolan, AMP | Will use existing ROW? How are you using it? | AEP | Will build in sections between stations.
SRRTEP-W | 2018-04-17 | Ryan Dolan, AMP | Circuit will be retired? | AEP | Not with this project. Coordination required. Will bring a separate project to address.
SRRTEP-W | 2018-04-17 | Ryan Dolan, AMP | Expect to retire line? | AEP | Yes.
SRRTEP-W | 2018-04-17 | Ryan Dolan, AMP | Why not just one CB, rather than 2 CB? | AEP | One CB would have dropped too much load.
SRRTEP-W | 2018-04-17 | Ryan Dolan, AMP | Why not alternating MOABs and CB? | AEP | Think this has the best cost/benefit ratio.
SRRTEP-W | 2018-04-17 | Ryan Dolan, AMP | Skip span construction? | DEOK | Do you believe that is this the case.
SRRTEP-W | 2018-04-17 | Ryan Dolan, AMP | Are do cap switchers op independently? | AEP | Yes
SRRTEP-W | 2018-04-17 | Ryan Dolan, AMP | Justification of bus tie breaker | AEP | cutting bus fault exposure.
SRRTEP-W | 2018-04-17 | Ryan Dolan, AMP | Why not a ring? | AEP | Have to get back on that. Space constrained. Always something. But no not much.
SRRTEP-W | 2018-04-17 | Ryan Dolan, AMP | Wasn't another project proposed today in this area. | AEP | Close. Bendix Tap, Hickory Creek.
SRRTEP-W | 2018-04-17 | Ryan Dolan, AMP | Looked into optimizing projects? | AEP | Yes.
SRRTEP-W | 2018-04-17 | Ryan Dolan, AMP | Is that planning process open to the public? | AEP | No. Do meet with customers
SRRTEP-W | 2018-04-17 | Ryan Dolan, AMP | How do we apply these projects to the current RTEP? | PJM | Come back around after wards
SRRTEP-W | 2018-05-21 | Ryan Dolan, AMP | Another project in the area? | PJM | Poss. Looking. Gen proj coming out of suspension. Not part of their study. This is a result of load changes.
SRRTEP-W | 2018-05-21 | Ryan Dolan, AMP | Reason serve customers from 138kV vs. 69kV? | ATSI | More cost effective.
SRRTEP-W | 2018-05-21 | Ryan Dolan, AMP | S/C extension? | ATSI | Yes.
SRRTEP-W | 2018-05-21 | Ryan Dolan, AMP | Related to performance of existing syste? | ATSI | Related to D upgrade. Could be reliability, switching options.
SRRTEP-W | 2018-05-21 | Ryan Dolan, AMP | Ready in 2 months? | ATSI | Check. May be a typo
SRRTEP-W | 2018-05-21 | Ryan Dolan, AMP | Project costs going down but will miss date? | DUQ | Customer changing so had to delay.
SRRTEP-W | 2018-05-21 | Ryan Dolan, AMP | Standard methodology for prioritization? | DEOK | No published standards. Asset Mgmt has a meth but planning is not aware of it.
SRRTEP-W | 2018-05-21 | Ryan Dolan, AMP | Still scoping? | DEOK | Sure it is on the brink of engineering. Easy to build.
SRRTEP-W | 2018-05-21 | Ryan Dolan, AMP | Steel or wood construction? | DEOK | Vast majority are steel.
SRRTEP-W | 2018-05-21 | Ryan Dolan, AMP | Leaving old line in place? | AEP | Until new line is rebuilt. Costs for removal included.
SRRTEP-W | 2018-05-21 | Ryan Dolan, AMP | Poss. Another project to address radial? | AEP | Possibly, yes.
SRRTEP-W | 2018-05-21 | Ryan Dolan, AMP | Was D/C considered? | AEP | Not sure.
SRRTEP-W | 2018-05-21 | Ryan Dolan, AMP | New ROW? | AEP | No. Believe can squeeze in existing. Will ask Jasmine to follow up on why not building D/C. Probably insuff. ROW.
SRRTEP-W | 2018-05-21 | Ryan Dolan, AMP | What alternatives were considered? | AEP | Based on condition. No viable alternatives identified.
SRRTEP-W | 2018-05-21 | Ryan Dolan, AMP | Suggestion. | AEP | Can we follow up off-line? Not sure I will get it.
SRRTEP-W | 2018-05-21 | Ryan Dolan, AMP | Eliminate bulk of 69kV rebuild, and tie into 138kV. Muni's have 69kV feeds. | AEP | will consider.
SRRTEP-W | 2018-05-21 | Ryan Dolan, AMP | Softail switch? | AEP | Replacing hard tap with a switch.
SRRTEP-W | 2018-05-21 | Ryan Dolan, AMP | Is this a separate project? | AEP | Poss. But working in the area, same yard. Elected to combine.
SRRTEP-W | 2018-05-21 | Ryan Dolan, AMP | Ligonier will stay in service? How does this address issue? | AEP | Yes.
SRRTEP-W | 2018-05-21 | Ryan Dolan, AMP | Glandorf is replacing Ottawa? Same footprint? | AEP | Yes. Believe moved slightly due to flooding issues. Will get back to you.
SRRTEP-W | 2018-05-21 | Ryan Dolan, AMP | ?? | AEP | Will have to get back to you. There are a couple of stations wrapped in s1616.2. Should split out. Will have to get back to you.
SRRTEP-W | 2018-05-21 | Ryan Dolan, AMP | Wondered that cost is almost $2M/mi. Why? | AEP | Don't have estimate. Will have to follow up
SRRTEP-W | 2018-05-21 | Ryan Dolan, AMP | Build by AEP crews? | AEP | Do not know
SRRTEP-W | 2018-05-21 | Ryan Dolan, AMP | Estimates are correct? | AEP | As far as I know.
SRRTEP-W | 2018-05-21 | Ryan Dolan, AMP | Same construction as Ottawa project? | AEP | Yes. Can not explain discrepancy at this point. Could follow up.
SRRTEP-W | 2018-05-21 | Ryan Dolan, AMP | How many CB? Only 4 elements in ring? | AEP | 6 CB ring. Yes, 4 elements so breaker & half. No I read it wrong. 6 elements on the bus.
SRRTEP-W | 2018-05-21 | Ryan Dolan, AMP | Station service not moving? | AEP | Correct. Does not move.
SRRTEP-W | 2018-05-21 | Ryan Dolan, AMP | Keeping the cap bank? | AEP | Removing it. Not sure of age or condition, so no sure it reusing or using parts.
SRRTEP-W | 2018-05-21 | Ryan Dolan, AMP | How decide to remove? | AEP | Have a method.
SRRTEP-W | 2018-05-21 | Ryan Dolan, AMP | How many ops on CB C at West Canton? What model? | AEP | Do not have. Will follow up
SRRTEP-W | 2018-05-21 | Ryan Dolan, AMP | 6 CB ring necessary? | AEP | Building in the clear, so don't want to limit.
SRRTEP-W | 2018-05-21 | Ryan Dolan, AMP | Condition of steel? | AEP | Wood at lower voltages, so all being replaced.
SRRTEP-W | 2018-05-21 | Ryan Dolan, AMP | How related to Adams-Riordan project. | AEP | Close but separate
SRRTEP-W | 2018-05-21 | Ryan Dolan, AMP | So D/C is ok here but can't rebuild as D/C on the prior project? | AEP | Jasmine previously stated, no existing ROW for D/C.
SRRTEP-W | 2018-05-21 | Ryan Dolan, AMP | considered a voltage conversion? | AEP | Can't say would need to follow-up
SRRTEP-W | 2018-05-21 | Ryan Dolan, AMP | Large 34kV rebuild in the area? | AEP | Large rebuild further north. Generally don't rebuild 34.5kV
SRRTEP-W | 2018-05-21 | Ryan Dolan, AMP | Looked at projects as a whole? | AEP | Valley upgrades are isolated. This 138kV line is a prime corridor. Not sure how a 34kV line would impact this.
SRRTEP-W | 2018-05-21 | Ryan Dolan, AMP | Why not convert ot 138kV | AEP | Can't say. Not sure that it wasn't considered.
SRRTEP-W | 2018-05-21 | Ryan Dolan, AMP | Alternatives considered? | AEP | As mentioned last time, several options. Line was in poor condition. 138kV may be possible. Lots of other 69kV in the area, so made sense to keep.
SRRTEP-W | 2018-05-21 | Ryan Dolan, AMP | Why not bring 138kV into Shadyside and eliminate a big chunk of 69kV? | AEP/PJM | Not convinced that 138kV option is effective. Also not sure we want to release ROW. Terrain is hilly, lots of residential. Acquiring add'l ROW would be challenging. /Since next meeting is 5/30/2018. Suggest that we cancel upcoming meeting and add a meeting in June 2018.
SRRTEP-W | 2018-05-21 | Ryan Dolan, AMP | Request to keep the 5/30 meeting, so can get answers to questions. A lot of issues with "don't know". | AEP | Believe have been answering your questions. At least those that are pertinent to the project.
SRRTEP-W | 2018-05-21 | Ryan Dolan, AMP | Follow up on 345kV work? | ComED | That was a TEAC meeting. It will stay in TEAC.
SRRTEP-W | 2018-12-18 | Ryan Dolan, AMP | Conductor sizes? | AEP | On slides.
SRRTEP-W | 2018-12-18 | Ryan Dolan, AMP | Are the distrib stations in adequate conditions? Need any work? | AEP | Don't have that info.
SRRTEP-W | 2018-12-18 | Ryan Dolan, AMP | Was wood poles considered? | AEP | Always an option. Not sure why steel was chosen.
SRRTEP-W | 2018-12-18 | Ryan Dolan, AMP | Report back on cost of wood? | AEP | Not sure that wood was costed.
SRRTEP-W | 2018-12-18 | Ryan Dolan, AMP | Why only replacing only highway crossing? | AEP | Rest of line was ok.
SRRTEP-W | 2018-12-18 | Ryan Dolan, AMP | Fault ops on 345kV CB? | AEP | Don't have that info. Not replacing, so not relevant.
SRRTEP-W | 2018-12-18 | Ryan Dolan, AMP | Age of transformers? | AEP | Don't have D-transformer.
SRRTEP-W | 2018-12-18 | Ryan Dolan, AMP | Fault | AEP | 56, 32,32,7,521, 26
SRRTEP-W | 2018-12-18 | Ryan Dolan, AMP | why replace CB with only 7 ops? | AEP | oil breaker, replacing while working at substation
SRRTEP-W | 2018-12-18 | Ryan Dolan, AMP | How many oil breakers on system. | AEP | Don't have, not relevant to replacement
SRRTEP-W | 2018-12-18 | Ryan Dolan, AMP | Track I^2T? | AEP | Can't track on electro-mech CB
SRRTEP-W | 2018-12-18 | Ryan Dolan, AMP | How many CB faults are related to MOAB ops? | AEP | Don't have that info. Can't tell what caused the fault.
SRRTEP-W | 2018-12-18 | Ryan Dolan, AMP | Distrib costs break out? | AEP | While update cost on slides.
SRRTEP-W | 2018-12-18 | Ryan Dolan, AMP | Highland Ave, only 2 sources? | AEP | No 3.
SRRTEP-W | 2018-12-18 | Ryan Dolan, AMP | MOABs? | AEP | 2 MOABs on the through path.
SRRTEP-W | 2018-12-18 | Ryan Dolan, AMP | Radial customer on Woster (Orville AMP customer) | AEP | Have been talking with Orville. Not directly involved in project. They are aware of work.
SRRTEP-W | 2018-12-18 | Ryan Dolan, AMP | Wood or steel? | AEP | No idea.
SRRTEP-W | 2018-12-18 | Ryan Dolan, AMP | Relay upgrades at E. Wooster. Coordinated with Orville? | AEP | Not sure impacting 138kV. Will if it does impact them.
SRRTEP-W | 2018-12-18 | Ryan Dolan, AMP | Switches on through path 138kV, how was this not a T cost? | AEP | State tariff, cost to customer
SRRTEP-W | 2018-12-18 | Ryan Dolan, AMP | Status? | AEP | Probably will start construction soon. Engin 15 days max.
SRRTEP-W | 2018-12-18 | Ryan Dolan, AMP | How this project addr the old line with open conditions? | AEP | Can't address the driver without this project in place.
SRRTEP-W | 2018-12-18 | Ryan Dolan, AMP | Why not addressing specific condition? Why not build d/c? | AEP | Can't address problem without doing this project. Have existing ROW. Better reliability for 2 S/C than one d/c.
SRRTEP-W | 2018-12-18 | Ryan Dolan, AMP | This contradicts argument used for Sheridan. | AEP | Situations are not equivalent.
SRRTEP-W | 2018-12-18 | Ryan Dolan, AMP | Fault duties to breakers | AEP | Request from PJM
SRRTEP-W | 2018-12-18 | Ryan Dolan, AMP | Why build 138kV station? | AEP | Considering converting the whole area?
SRRTEP-W | 2018-12-18 | Ryan Dolan, AMP | Is there a scope to update that area? | AEP | Very conceptual, still vetting.
SRRTEP-W | 2018-12-18 | Ryan Dolan, AMP | How many stations to update? | AEP | Will look into.
SRRTEP-W | 2018-12-18 | Ryan Dolan, AMP | New load or transferred? | AEP | Mostly transferred, will need to follow-up
SRRTEP-W | 2018-12-18 | Ryan Dolan, AMP | Line has been overloading. Coord with neighbor? | AEP | Not aware of any overload. Overload is on the transformer.
SRRTEP-W | 2018-12-18 | Ryan Dolan, AMP | How does PJM handle this issue? | PJM | Communicate with external. Up to them to address.
SRRTEP-W | 2018-12-18 | Ryan Dolan, AMP | What is the current and upgraded limits? | AEP | 675MVA. Upgrade risers to ensure conductor is not
SRRTEP-W | 2018-12-18 | Ryan Dolan, AMP | How obtain that MSLE and upgrade information? | PJM | Will have the conversation. Massive workload
SRRTEP-W | 2018-12-18 | Ryan Dolan, AMP | More detail on when coal pays and when not. | AEP | Customer is paying for the extended service. These are existing deficiencies on line that need to be addressed.
SRRTEP-W | 2018-12-18 | Ryan Dolan, AMP | Update slide to say replace not reinforce? | AEP | Yes.
SRRTEP-W | 2018-12-18 | Ryan Dolan, AMP | At what station were outages occurring. | AEP | Will not be providing that detail.
SRRTEP-W | 2018-12-18 | Ryan Dolan, AMP | So no idea if switches are effective at addressing issues. | AEP | There is additional info used in making determination.
SRRTEP-W | 2018-12-18 | Ryan Dolan, AMP | Addressing line issue? | AEP | Yes. Renaming line, building Kalamazoo sta. Need to do this so not to drop load.
SRRTEP-W | 2018-12-18 | Ryan Dolan, AMP | Vicks-School line, place between 2 CBs at Kalamazoo. And then limit CB to 10 fault ops. Are we going to pre-maturally fail CBs | AEP | That is one criteria.
SRRTEP-W | 2018-12-18 | Ryan Dolan, AMP | As stakeholders, this is all we have age to determine. | AEP | Disagree. Many factors identified. These are qualitative data.
SRRTEP-W | 2018-12-18 | Ryan Dolan, AMP | Need it to be quantitative. That's what drives decision. | AEP | Agree but still need to use engineering judgement.
SRRTEP-W | 2018-12-18 | Ryan Dolan, AMP | What are the causes of the outages? | AEP | Not providing that detail.
SRRTEP-W | 2018-12-18 | Ryan Dolan, AMP | Is the in-service date correct? | AEP | Believe so.
SRRTEP-W | 2018-12-18 | Ryan Dolan, AMP | Was 556 kcmil considered? | AEP | Yes. Matched other existing lines.
SRRTEP-W | 2018-12-18 | Ryan Dolan, AMP | T - line was the could of upgrades? | AEP | Yes.
SRRTEP-W | 2018-12-18 | Ryan Dolan, AMP | What happens to CB? | AEP | use as spare or parts.
SRRTEP-W | 2018-12-18 | Ryan Dolan, AMP | Why not wait on the breaker? | AEP | If do all this now, then So Bend is ready for 69kV conversion.
SRRTEP-W | 2018-12-18 | Ryan Dolan, AMP | Any redundant CB's that retiring? | AEP | Can't answer at that time.
SRRTEP-W | 2018-12-18 | Ryan Dolan, AMP | Wanted to bring back Sheridan? | AEP | Discussing on private call on Friday.
TEAC | 2018-01-11 | Ryan Dolan, AMP | TannerCreek-Fort, incl OVEC in analysis. | PJM | Yes. No concerns.
TEAC | 2018-01-11 | Jon Syner, FE | Weren't there ME projects for these? | PJM | Some reliability projects.
TEAC | 2018-01-11 | Jon Syner, FE | Wouldn't acceleration elim need for ME projects? | PJM | No already considered in model.
TEAC | 2018-01-11 | Ryan Dolan, AMP | Look at FG files. Clifty-Dearborn not included. Concern about impact. | PJM | Will look at?
TEAC | 2018-01-11 | Adam Weber, Ameren | Do look to see that it doesn't just shift congestion? | PJM | Yes.
TEAC | 2018-01-11 | Ryan Dolan, AMP | When Crane gen deactiv? | PJM | Summer 2018
TEAC | 2018-01-11 | ?? | How model VFT? | PJM | Take off line. It is modelled.
TEAC | 2018-01-11 | Adam Weber, Ameren | When did final case post? Running analysis now. | PJM | Agreed. Will try to do better.
TEAC | 2018-01-11 | Adam Weber, Ameren | B/C rationon Slide 14 on how many sim years? | PJM | 4 yrs.
TEAC | 2018-01-11 | Adam Weber, Ameren | Think that is premature to recommend a project without all analysis completed. | PJM | Following the process. Hard for a ~$100M project to compete with an upgrade.
TEAC | 2018-01-11 | Adam Weber, Ameren | Steps left. Just constructability? | PJM | Constructability is proceeding. Seems reasonable.
TEAC | 2018-01-11 | Adam Weber, Ameren | Bundled conductors seems hard to believe without structure replacements. | PJM | cannot really eval until detailed engineering.
TEAC | 2018-01-11 | Sharon Segnor, LS Power | Update on 9A as well? | PJM | Can do that.
TEAC | 2018-01-11 | Adam Weber, Ameren | Feel that PJM is premature adding 5E into model without additional analysis. | PJM | Will consider.
TEAC | 2018-01-11 | Jon Syner, FE | Changes to Linden, Hoboken? | PJM | Yes.
TEAC | 2018-01-11 | Greg Paulson, Consumer Advocates | Generation at-risk scenario? Thinking about nukes. | PJM | ok.
TEAC | 2018-01-11 | Ryan Dolan, AMP | Assumptions with non-firm for Linden, Hoboken? | PJM | Reaches into test procedures. It depends on the procedure.
TEAC | 2018-01-11 | Ryan Dolan, AMP | Not clear. | PJM | Will look into. Expect treat as energy from gen.
TEAC | 2018-01-11 | James Manning, NCEC | Look at where recent winter loads land in relation to forecast. | PJM | Good comment. Will look into. Also, discussed at OC. Consider that it�s a 5 year average so a couple of extreme days do not cause big shift.
TEAC | 2018-01-11 | Ryan Dolan, AMP | Queue project has withdrawn. How does PJM handle? | PJM | At min, will study in 2018. If it impacts, will adjust. spikes in Apr due to gen outages.
TEAC | 2018-01-11 | Ryan Dolan, AMP | What line outages? | PJM | Can get data.
TEAC | 2018-01-11 | Ryan Dolan, AMP | Asked last time. Line is between shorts. Ok if charging. | PJM | Light load. Expect lines to be charging.
TEAC | 2018-01-11 | Ryan Dolan, AMP | voltage plots, MVARs, Lines out, gen out. Is this s real problem or just because of state of repairs. | PJM | Can provide data. But not an extreme outage. Believe it is a condition that needs addressed.
TEAC | 2018-01-11 | David Mabry, PJM Indust Customer Coal | Slide 11, more detail on statcoms | PJM/DOM | Sub bullets are part of definition of statcom. An array of fixed components auto-op to act as dynamic./ That is correct. Comes as a package.
TEAC | 2018-01-11 | ITC(?) | Diff. in high voltage limit? | DOM | Equipment limit. Both Dom & PJM Ops have requested a long term soln. It is real.
TEAC | 2018-01-11 | Ryan Dolan, AMP | Good point. Thanks. Would want some redundancy. It that included? Include shut reactors. | PJM | What does redundant mean?
TEAC | 2018-01-11 | Ryan Dolan, AMP | Why not put more shunts in? | PJM | Requires a lot of repairs. Not viable.
TEAC | 2018-01-11 | Ryan Dolan, AMP | Why not change size and add more? | PJM/DOM | Reactors switching are disruptive action. Can only be so big. Still repair issue./ Not an acceptable solution.
TEAC | 2018-01-11 | Ryan Dolan, AMP | Any reactors on system? | PJM | Yes on 230kV. Have had issues.
TEAC | 2018-01-11 | Ryan Dolan, AMP | What about thryristor reactor? | DOM | Studied. Sim cost, less capable.
TEAC | 2018-01-11 | Ed Tatum, AMP | Differences between bullets? | PJM | Basically the same.
TEAC | 2018-01-11 | Ed Tatum, AMP | What are the costs of the options? | PJM | Did not develop.
TEAC | 2018-01-11 | Ed Tatum, AMP | Looked at all the thermal & voltage violations? | PSEG | PSEG did and sent it to PJM.
TEAC | 2018-01-11 | Ryan Dolan, AMP | Need for D/C structures. Asked for highest MVA loading. | PJM | about 10% premium for D/C. Makes sense.
TEAC | 2018-01-11 | Ryan Dolan, AMP | What is the highest loading on the line possible? Diff. is the weight of the 1590kcmil on line. Is D/C really a good solution? | PSEG | line is 1590 today. Have seen it overloaded. 500kV at each end. Outages drop significant load on this line. Nuke in the area.
TEAC | 2018-01-11 | Ryan Dolan, AMP | Is it more prudent to string the second line now? | PSEG | No driver. Can consider.
TEAC | 2018-01-11 | Dave Pratzon, GT Power Group | Slide 24, recent metrics or 2013 metrics? | PJM | consultant study completed 2017, so all the data is from there?
TEAC | 2018-01-11 | Ed Tatum, AMP | Process question. Some questions that have not been addressed? | PJM | Go forward to board. Will continue to study.
TEAC | 2018-01-11 | Ed Tatum, AMP | how answer questions before go to board? | PJM | Open questions do not negate need or the recommendation.
TEAC | 2018-01-11 | Ryan Dolan, AMP | Does PJM have a procedure to approve the size of the conductor? | PJM | No. Part of the answer is up to the TO and related to engineering details. Can continue to discuss engineering details but does not impact the recommendation.
TEAC | 2018-01-11 | Ryan Dolan, AMP | How can move forward without such oversight? | PJM | An engineering decision.
TEAC | 2018-01-11 | Sharon Segnor, LS Power | wording of recommended solution. | PJM | should say d/c structures.
TEAC | 2018-01-11 | Sharon Segnor, LS Power | How did we get to d/c? | PJM | prudent based on 10% premium.
TEAC | 2018-01-11 | Ryan Dolan, AMP | Cannot say that. If the line overloads, we don't know how we would address this. | Calpine | Whether d/c is useful is a rate question.
TEAC | 2018-01-11 | Ed Tatum, AMP | Got money out of line. But have you shown that not replacing it is more expensive. | PSEG | Have studied. It makes sense.
TEAC | 2018-01-11 | Ryan Dolan, AMP | Number of fault ops on each CB? | AEP | 20, 58, 50, 33
TEAC | 2018-01-11 | Ryan Dolan, AMP | Manuf recomm? | AEP | 10
TEAC | 2018-01-11 | Ryan Dolan, AMP | Overload? | AEP | If don't replace existing single transformer, and loose line, would overload.
TEAC | 2018-01-11 | Ryan Dolan, AMP | Asked for simulationto show need series cap? | PJM | No have not. Can work with AEP.
TEAC | 2018-01-11 | Ryan Dolan, AMP | Transfer interface. PV analysis. Reactive interface is set in real time. | PJM | used reactor in recent cold snap.
TEAC | 2018-01-11 | Ryan Dolan, AMP | condition assessment of line? | AEP | Can look at it. Long line, 10 yr out before can address line.
TEAC | 2018-01-11 | Ryan Dolan, AMP | replacing 765 CB? | AEP | No, installing 3 new.
TEAC | 2018-01-11 | Ryan Dolan, AMP | Replacing transformers? | AEP | yes, trying to do in the clear. Significantly reduce downtime.
TEAC | 2018-01-11 | Ryan Dolan, AMP | Was going to talk with manuf about fault operations. | AEP | working on it.
TEAC | 2018-01-11 | Ryan Dolan, AMP | Dom talked about 100's. | AEP | talked about reactor switching vs. CB operating. Very different.
TEAC | 2018-01-11 | Sharon Segnor, LS Power | Board meeting? | PJM | Feb 12?
TEAC | 2018-01-11 | Ed Tatum, AMP | Make Board aware that there are questions still open the projects? | PJM | Will discuss.
TEAC | 2018-01-11 | Ryan Dolan, AMP | Some other projects taking to the board. | PJM | Yes, always do that.
TEAC | 2018-01-11 | Ryan Dolan, AMP | Hillsdale questions. CB ownership. Some are OVEC. | PJM | does it matter? Not aware of the details.
TEAC | 2018-03-08 | Adam Weber, Ameren | Report on cost analysis. | PJM | Preparing a white paper. Costs a little higher. Considering in selection
TEAC | 2018-03-08 | Adam Weber, Ameren | What inputs for 2031? | PJM | Some inputs.
TEAC | 2018-03-08 | Ryan Dolan, AMP | Most of reduction seems to be due to FSA. How much due to Supplemental? | PJM | Really cannot quantify that.
TEAC | 2018-03-08 | Ryan Dolan, AMP | Concern about how supplemental projects can impact. How notify stakeholders? | PJM | This is it.
TEAC | 2018-03-08 | Ryan Dolan, AMP | Why not a baseline? | PJM | The instability is being addressed by the RAS. This project was intended to eliminate the RAS, so no baseline driver.
TEAC | 2018-03-08 | Ryan Dolan, AMP | A lot going on in this area. What is the impact in the area? | PJM | This is part of the RTEP analysis.
TEAC | 2018-03-08 | Ryan Dolan, AMP | can we expand scope to include not just nuclear units but any unit with public documentation that retirement pending. | PJM | Yes.
TEAC | 2018-03-08 | ?? | What does "as-left" mean? | PJM | Where we left off study.
TEAC | 2018-03-08 | Dave Pratzon, GT Power Group | Include external units? | PJM | PJM does consider this.
TEAC | 2018-03-08 | Dave Pratzon, GT Power Group | Are we repeating the issues on MISO border that we did on the NY border? | PJM | dynamics are different.
TEAC | 2018-03-08 | Ryan Dolan, AMP | Address any issues below 150%? | PJM | No driver. 150% is a trigger for a closer look, but not a driver.
TEAC | 2018-03-08 | Ryan Dolan, AMP | No assets in the existing yard? | PJM | No. Costs are to remove equipment.
TEAC | 2018-03-08 | Ryan Dolan, AMP | Did PJM's PRA process identify this? | PJM | No, PRA is a sparing strategy.
TEAC | 2018-03-08 | Ryan Dolan, AMP | Disposition of old transformer? | PJM | Don't know.
TEAC | 2018-03-08 | Ryan Dolan, AMP | With respect to resilience, don't care how old they are. | PJM | Looking at two different issues.
TEAC | 2018-03-08 | Ryan Dolan, AMP | Gassing, carbonization, etc. part of | PJM | considered whether maintenance records are subject to disclosure.
TEAC | 2018-03-08 | Ryan Dolan, AMP | Asked before about overlapping zones of protection. Now adding CB's. Are there overlapping zones of protection? | PJM | Have to look into it.
TEAC | 2018-03-08 | Ryan Dolan, AMP | How can they get a transformer in place that fast? | PJM | We are adjusting the process. It will take time. Cannot delay projects now.
TEAC | 2018-03-08 | Ryan Dolan, AMP | Ask for consistency in the use of Project Status. Making PJM aware of capital investments. Are we locked in? | PJM | Not sure how far we go in disclosing company's financial plans.
TEAC | 2018-03-08 | Ryan Dolan, AMP | So we can expect no change in info? | PJM | Would not say that. If withhold info, does not imply no change.
TEAC | 2018-03-08 | Ryan Dolan, AMP | Will request one lines. Any impact on load deliv? | PJM | Will need to review.
TEAC | 2018-03-08 | Ryan Dolan, AMP | Written questions at last meeting? | PJM | Do not have those answers yet.
TEAC | 2018-03-08 | Ryan Dolan, AMP | Will these come back? | PJM | No.
TEAC | 2018-03-08 | Ryan Dolan, AMP | So If we comply with M-3, within time, will we get timely response? | PJM/BGE | We post when we get the answers./ CBs are 47 years of age, Jericho. Maintenance costs are very high. Oil testing procedures in place. Not sure if will share in the future. Not releasing make and model info.
TEAC | 2018-03-08 | Ryan Dolan, AMP | Questions in writing. | ComEd | None for Lisle.
TEAC | 2018-03-08 | Ryan Dolan, AMP | Response to written questions. | ComEd | Gnd break line in -service. Same station as circuit switcher
TEAC | 2018-03-08 | Ryan Dolan, AMP | Still part of cost recovery? | PJM | Not a PJM issue.
TEAC | 2018-03-08 | Ryan Dolan, AMP | How long window open? | PJM | 60 days. Registration will open by the end of March. Will take that into consideration
TEAC | 2018-04-05 | Ryan Dolan, AMP | Would impacts related to impacts be open to competitive process? | PJM | Statutory req. to respond in 60 days. No opportunity for a window.
TEAC | 2018-04-05 | Ryan Dolan, AMP | Where is violation happening? | PJM
TEAC | 2018-04-05 | Ryan Dolan, AMP | Analysis is N-1-1 or N-2? Adjust shunts? | PJM | N-1-1. No shunt adjustments. Not practical
TEAC | 2018-04-05 | Bill Pazella, ODEC | Isn't there a new load deliv in the area? | DOM | Yes, but on a different line. Was taken into account.
TEAC | 2018-04-05 | Ryan Dolan, AMP | Any issues to falling power south of Chesterfield | PJM | Power flow is not clear. Can study and get back to you.
TEAC | 2018-04-05 | Ryan Dolan, AMP | All violations or just open to competition? | PJM | All violations
TEAC | 2018-04-05 | Adam Weber, Ameren | Cases available to all stakeholders | PJM | Yes.
TEAC | 2018-04-05 | Jon Syner, FE | Register? | PJM | Yes
TEAC | 2018-04-05 | Dave Pratzon, GT Power Group | In on current rating of line. | PJM | Project will realize the ratings listed.
TEAC | 2018-04-05 | Ryan Dolan, AMP | Cost of AEP portion? | PJM | Follow up
TEAC | 2018-04-05 | Ryan Dolan, AMP | What happens if it reaches cost of alternatives? | PJM | Will bring back to
TEAC | 2018-04-05 | Ryan Dolan, AMP | Constructability assessment? | PJM | Not sure
TEAC | 2018-04-05 | Ryan Dolan, AMP | This is a condition assessment/ | PJM | Loading issue.
TEAC | 2018-04-05 | Ryan Dolan, AMP | What is the enabler? | PJM | Baseline work plus supplemental
TEAC | 2018-04-05 | Ryan Dolan, AMP | No supp needs in the area that would necessitate future upgrades? | PJM | That is our understanding.
TEAC | 2018-04-05 | Ryan Dolan, AMP | Cost of alternative? | PJM | Not available. Need to acquire ROW.
TEAC | 2018-04-05 | Ryan Dolan, AMP | Any system reconfig? | PJM | Nothing that was satisfactory.
TEAC | 2018-04-05 | Ryan Dolan, AMP | Was Hyatt re-conductor considered? | PJM | Won't solve all the issues.
TEAC | 2018-04-05 | Ryan Dolan, AMP | Not aware of any structural issues on the line. Necessitate rebuild. | AEP | woodpecker holes in wood. Poles will not support additional conductor.
TEAC | 2018-04-05 | Ryan Dolan, AMP | Additional detail on age, d/c portion etc. | AEP | Believe all that info in on slides.
TEAC | 2018-04-05 | Ryan Dolan, AMP | Did the IPP drive the need for the sub? | PJM | Not sure. Old project. Not sure we can find out.
TEAC | 2018-04-05 | Ryan Dolan, AMP | so do gen have to pay for changes? | PJM | Gen are not responsible. Line is within PJM.
TEAC | 2018-04-05 | Ryan Dolan, AMP | Age of transformer | AEP | 1980 vintage
TEAC | 2018-04-05 | Ryan Dolan, AMP | Do you maintain the transformer? | AEP | Yes. Previously doc
TEAC | 2018-04-05 | Ryan Dolan, AMP | Reactors in-service? | AEP | Not sure.
TEAC | 2018-04-05 | Ryan Dolan, AMP | Perhaps use reactors to extend lfe of transformer? | AEP | Beyond EOL.
TEAC | 2018-04-05 | Ryan Dolan, AMP | Instead of switchable spare, consider.. | AEP | Think we already have that.
TEAC | 2018-04-05 | Ryan Dolan, AMP | Operational response? | AEP/PJM | Can't say./ Don't recall any issues. Can check.
TEAC | 2018-04-05 | Ryan Dolan, AMP | are you changing the line connection? | AEP | No changes. Moving one line off the bus. 345kV side.
TEAC | 2018-04-05 | Ryan Dolan, AMP | Still conceptual? | PJM | No info that is in engineering
TEAC | 2018-05-03 | Ryan Dolan, AMP | Thanks for posting prelims. Any idea how many will be open to competition? Could we have a single window? | PJM | Agree it looks light this year. But don't want to delay proposals. Don't want to roll over into next year with window.
TEAC | 2018-05-03 | Ryan Dolan, AMP | Supplementals not studied in case? Will there be a case with all those supplements applied? | PJM | Not sure. Depends on workload. Can't commit yet.
TEAC | 2018-05-03 | Carl Johnson, Customized Energy Solutions | Concern about narrative. How much is the address immediate load growth? How much is future and immediate. | PJM | 100MVA load growth is immediate. Additional load growth later. Additional 160 MVA is projected.
TEAC | 2018-05-03 | Ryan Dolan, AMP | Overloads id at what level? | PJM | 440 MVA. Believe 100 of 160 is immediate.
TEAC | 2018-05-03 | Ryan Dolan, AMP | Existing plan for the 280MVA. 160 MVA is on top. What is the overload? | PJM | Need to get back to you.
TEAC | 2018-05-03 | Ryan Dolan, AMP | What is overloading and possible impact to supplements. | PJM | Is point to point circuit.
TEAC | 2018-05-03 | Ryan Dolan, AMP | Is this accounting for other issues? | PJM | ??
TEAC | 2018-05-03 | John, Nexterra | Only 60 committed, and 100 planned? | PJM | reversed.
TEAC | 2018-05-03 | John Horstman, Dayton | Need date? | PJM | June 1, 2019
TEAC | 2018-05-03 | Ryan Dolan, AMP | 2 things drive overloads | PJM | small areas. Load is driving.
TEAC | 2018-05-03 | Ryan Dolan, AMP | Is this all immediate need. What are the scenarios in which we would see competitive upgrades? | PJM | Really not possible for PJJM to project these types of load growth.
TEAC | 2018-05-03 | Ryan Dolan, AMP | More of a process question. Are we never asking for 15 year load projection? No way to project? Shouldn't we be scaling for shale gas? | PJM | Yes, but can't expect. There are many test wells. Can't predict if site will be viable.
TEAC | 2018-05-03 | Ryan Dolan, AMP | Uplift | PJM | 2017 $13M. Been steadily increasing. This cuts them off.
TEAC | 2018-05-03 | Ryan Dolan, AMP | Voltage of risers at DE | AEP | at DE it is all 138kV work.
TEAC | 2018-05-03 | Ryan Dolan, AMP | Voltage risers at Twin Branch, South Bend | AEP | 138kV
TEAC | 2018-05-03 | Ryan Dolan, AMP | Any other work going on this area? Quite expensive. | AEP | will need to look at wording. Probably to re-term, lines. Will follow up
TEAC | 2018-05-03 | Ryan Dolan, AMP | Work at German? | AEP | Do not allow 4 MOABS on a line.
TEAC | 2018-05-03 | Ryan Dolan, AMP | Another project is removing a MOAB with a CB, so should only be 3 MOABS on line. | AEP | will need to review.
TEAC | 2018-05-03 | Ryan Dolan, AMP | all retirement studies included in cancellation? | PJM | Will double check
TEAC | 2018-05-03 | Adam Weber, Ameren | ?? | PJM | Yes.
TEAC | 2018-05-03 | Adam Weber, Ameren | Seeing overloads in Peach Bottom - ?? Line. Would ME project be reconcidered? | PJM | we do constantly reeval. It may be come back.
TEAC | 2018-05-03 | Ryan Dolan, AMP | Believe it is being discussed in the ME upgrade? | PJM | Not sure. Will try to bring in an update to the TEAC.
TEAC-GenDeactiv | 2018-05-03 | Industrial Power coalition | Davis-Besse, accelerating existing baseline projects. Is that correct | PJM | Yes.
TEAC-GenDeactiv | 2018-05-03 | Miles Taylor, Mscope | What are the details.
TEAC-GenDeactiv | 2018-05-03 | Ryan Dolan, AMP | Have all the baseline projects that need to be accelerated been ID'd? | PJM | Yes.
TEAC-GenDeactiv | 2018-05-03 | Ryan Dolan, AMP | There are additional projects needed? | PJM | Yes
TEAC-GenDeactiv | 2018-05-03 | Ryan Dolan, AMP | if projects are more that 3yrs out, no competitive projects? | PJM | Yes.
TEAC-GenDeactiv | 2018-05-03 | Ryan Dolan, AMP | See prelim flowgates with gen deactiv is driving. Will those be open to competition | PJM | Deactivation study is 3 years out.
TEAC-GenDeactiv | 2018-05-03 | Ryan Dolan, AMP | Test is looking at PJM capacity issues. Include energy as well? | PJM | Yes. Was getting there. Include energy in common mode analysis.
TEAC-GenDeactiv | 2018-05-03 | Ryan Dolan, AMP | Load deliv? What margin is left? | PJM | Analysis only looks at CETL levels. CETO/CETL is part of the TP analysis, not the deactiv. Study.
TEAC-GenDeactiv | 2018-05-03 | Ryan Dolan, AMP | With amount of gen retire, and issue with reactive inputs and consider economic impacts? | PJM | reactive limits applied at this study?
TEAC-GenDeactiv | 2018-05-03 | Ryan Dolan, AMP | are we going to go into summer peak load and have reactive load limits? | PJM | Not part of the study.
TEAC-GenDeactiv | 2018-05-03 | Ryan Dolan, AMP | PJM sets reactive limits. Are they being adjusted? | PJM | Yes, we have looked at these and don't see any issues. The "new" definition of the reactive interface are just relative to ops. It only is to provide additional ops flexibility.
TEAC-GenDeactiv | 2018-05-03 | Scarpa, Calpine | With FE studies completed. | PJM | Completed. Will verify that info is updated. Reliability is final. Just refining costs. Will present in June. In past with large deactiv., need to turn around in 30 days. Sometimes not the best solution so there may be some changes.
TEAC-GenDeactiv | 2018-05-03 | Ryan Dolan, AMP | Contact all TO in the area if see issues? | PJM | Contact everyone who is impacted.
TEAC-GenDeactiv | 2018-05-03 | Ryan Dolan, AMP | Contact all owners who might be able to correct solution? | PJM | Yes.
TEAC-ME | 2018-02-08 | Carl Johnson, Customized Energy Solutions | Savings is annual? | PJM | Yes.
TEAC-ME | 2018-02-08 | Adam Weber, Ameren | Asterisk on cost field in Sept. But not change. Any update? | PJM | Some question about some cost. But they were not significant.
TEAC-ME | 2018-02-08 | Ryan Dolan, AMP | b2752, were CB replacements, included in that analysis? | PJM | Yes. We included all the infrastructure. Delta would be well within the contingency.
TEAC-ME | 2018-02-08 | Adam Weber, Ameren | Guideline on acceptable vs. unacceptable congestion shift. | PJM | Will address tomorrow
TEAC-ME | 2018-02-08 | Sharon Segnor, LS Power | Does constructability analysis consider pending MD environmental legislation? | PJM | Considered an upgrade, needing no add'l ROW, so should have no impact.
TEAC-ME | 2018-02-08 | Adam Weber, Ameren | Structures can handle the load of the add'l conductors? | PJM | Yes.
TEAC-ME | 2018-02-08 | Adam Weber, Ameren | Will PJM publish an analysis for all ME upgrades in one case? | PJM | That was relative to the number of small projects. Not really an issue hear.
TEAC-ME | 2018-02-08 | Sharon Segnor, LS Power | How to handle the new REGI regs? | PJM | will include the fuel fcst . Assumptions will be discussed in TEAC
TEAC-ME | 2018-02-08 | Adam Weber, Ameren | Please publish base case and events file asap. A lot of info to vet and chg. | PJM | Will do.
TEAC-Reliability | 2018-02-08 | Ed Tatum, AMP | is the assessment of condition by PJM or PSEG? | PJM | Certainly seems reasonable.
TEAC-Reliability | 2018-02-08 | Ryan Dolan, AMP | Why is there such difference in costs. No info on justifying the d/c or the cost difference. | PJM | Have discussed d/c and delta last time. The projects were estimated at diff time, with diff. methodology and to different leave of detail.
TEAC-Reliability | 2018-02-08 | Ryan Dolan, AMP | Is that PJM's experience for cost difference? | PJM | Not sure we even have that info.
TEAC-Reliability | 2018-02-08 | Dave Pratzon, GT Power Group | What analysis was done on line? | PJM | NERC N-1 analysis. Thermal and Voltage. Saw many, severe issues so stopped analysis. Indicates that the remove and retire is a bad idea.
TEAC-Reliability | 2018-02-08 | Dave Pratzon, GT Power Group | Should PSEG ratepayers pay cost, or is it a JCPL cost? | PJM | Project decision cannot be made based on cost allocation.
TEAC-Reliability | 2018-02-08 | Ryan Dolan, AMP | Any reinforcements to temper the construction cost? | PJM/PSEG | To provide support to all the stations on the line, essentially replace the line. Makes no sense/ Looked at all the alternatives you suggested. None of them are viable.
TEAC-Reliability | 2018-02-08 | Ed Tatum, AMP | Cost to upgrade 34.5kV system in JCPL? Wouldn't that be a worth considering? | PJM | The magnitude of the issue will not be resolved by 34.5kV upgrades.
TEAC-Reliability | 2018-02-08 | Ryan Dolan, AMP | What is the projected in-serv. | AEP | will coord with other CB work. In 2018
TEAC-Reliability | 2018-02-08 | Ryan Dolan, AMP | OVEC integration overload due to one of these breakers. | PJM | Cannot say at this time.
TEAC-Reliability | 2018-02-08 | Ryan Dolan, AMP | How does PJM ensure that Tos are bringing info to PJM? | PJM | We asked them.
TEAC-Reliability | 2018-02-08 | Ryan Dolan, AMP | It is happening now. How do we fix this? | PJM | Having that info internally. More information to come.
TEAC-Reliability | 2018-02-08 | Ryan Dolan, AMP | Cost is for 4 230kV CB? | BGE | Yes.
TEAC-Reliability | 2018-02-08 | Ryan Dolan, AMP | Line breakers, no ring bus. Standard for line breakers? | ComEd | No. Standard is breaker & half. Not cost effective to rebuild that way.
TEAC-Reliability | 2018-02-08 | Ryan Dolan, AMP | Why avoid tertiary? | ComEd | Tertiary causes overloads on transformer taps and failure.
TEAC-Reliability | 2018-02-08 | Ryan Dolan, AMP | Issue? | ComEd | This type of transformer cannot be reblanked. No repairs possible.
TEAC-Reliability | 2018-02-08 | Ryan Dolan, AMP | Scrapping transformer? | ComEd | Yes.
TEAC-Reliability | 2018-02-08 | Ryan Dolan, AMP | Fault ops? | AEP | 20, 50, 33 fault ops.
TEAC-Reliability | 2018-02-08 | Ryan Dolan, AMP | Replacing all PK CBs? | AEP | Yes, replacing air-blast CB.
TEAC-Reliability | 2018-02-08 | Ryan Dolan, AMP | Can you provide an idea of how many? | PJM | Work on that.
TEAC-Reliability | 2018-02-08 | Ryan Dolan, AMP | Do any stakeholders have the 2018 case yet? | PJM | No.
TEAC-Reliability | 2018-02-08 | Ed Tatum, AMP | Answer questions in writing? When? | PJM | Yes. About a week?
TEAC-Reliability | 2018-02-08 | Ed Tatum, AMP | Stat updates? | PJM | In the next day or two.