## toPlanning ME Congestion
Note: The initial congestion results from the work-in-progress ME Case are shared for transparency purposes and to ensure PJM has the most accurate info in its models. The results shared represent an early assessment and still need refinement*. Updated results will be posted once the Preliminary ME Base Case is finalized.
[6 empty] | Annual congestion ($)* |  | Binding Hours
Monitored Branch Full Name | Contingency | To Area | From Area | To Voltage Level | From Voltage Level | 2027 | 2030 | 2027 | 2030
AP South Interface | BLACKO-BEDNG |  |  |  |  | 48617121.42 | 97912935.49 | 1201 | 1716
Black Oak Bedington Interface | BASE CASE |  |  |  |  | 50170675.28 | 79606647.5 | 781 | 754
Messick Rd-Morgan 138 kV | AP_P1-2_WP-500-DRT17_SRT-SL | APS | APS | 138 | 138 | 45794373.75 | 61789698.63 | 1187 | 1630
Safe Harbor-Graceton 230 kV | PECO_P1-2_5012_SRT-A/* $ CHESCO $ PECO_P1-2_5012 | PLGRP | BGE | 230 | 230 | 25880530.86 | 24846458.77 | 1491 | 1356
Germantown-Straban 115 kV | PJM_500_BG_P1_5011_SRT-A | METED | METED | 115 | 115 | 5226060.72 | 17341758.71 | 425 | 1064
Shade Gap-Roxbury 115 kV | AP_P1-2_WP-500-DRT17_SRT-SL | PENELEC | PENELEC | 115 | 115 | 694743.05 | 16257440.64 | 110 | 677
Dumont-Stillwell 345 kV | AEP_P1-2_#695_1681 | AEP | NIPS | 345 | 345 | 9881912.64 | 12911728.93 | 321 | 399
Straban-Lincoln 115 kV | PJM_500_BG_P1_5011_SRT-A | METED | METED | 115 | 115 | 3548520.2 | 9388191.13 | 97 | 196
Olive-Univ. Pk. N. 345 kV | AEP_P1-2_#695_1681 | AEP | COMED | 345 | 345 | 4747690.07 | 9330308.25 | 150 | 235
AEP DOM Interface | BASE CASE |  |  |  |  | 714781.62 | 6026534.34 | 47 | 162
Krendale-Shanor Manor 138 kV | AP-P1-2-WP-500-302T | APS | APS | 138 | 138 | 889473.14 | 4935645.99 | 35 | 112
Dans Mountain-Ridgeley 138 kV | AP-P1-2-PE-500-004 | APS | APS | 138 | 138 | 2354423.88 | 4690128.9 | 379 | 452
Shade Gap-Roxbury 115 kV | AP_P1-2_WP-500-DRT17_SRT-SL | PENELEC | PENELEC | 115 | 115 | 630501.45 | 4614268.28 | 110 | 340
Haumesser Rd. (R)-W De Kalb Tap (R) 138 kV | COMED_P1-2_345-L15502_B-R | COMED | COMED | 138 | 138 | 3234890.09 | 4110887.83 | 153 | 165
Shade Gap-Roxbury 115 kV | BASE CASE | PENELEC | PENELEC | 115 | 115 | 474087.52 | 3406125.78 | 103 | 483
Fieldale-Thornton 138 kV | AEP_P1-2_#311_5_SRT-A | AEP | AEP | 138 | 138 | 3424998.38 | 3327775.91 | 68 | 84
T131 TR-Logtown 138 kV | BASE CASE | AEP | AEP | 138 | 138 | 2858381.21 | 3270104.6 | 269 | 269
Goose Creek-Ashburn 230 kV 2 230 kV | DVP_P1-2: LN 274 | DOM | DOM | 230 | 230 | 0 | 3128080.09 | 0 | 42
Dickerson-H-Dickerson 230 kV | PEPCO_P1_PP1 | PEPCO | PEPCO | 230 | 230 | 318364.73 | 3077211.46 | 58 | 137
East Danville-Banister 138 kV | AEP_P1-2_#311_5_SRT-A | AEP | AEP | 138 | 138 | 1461085.61 | 3066493 | 55 | 126
ESS H452-Waterman 138 kV | BASE CASE | COMED | COMED | 138 | 138 | 2695586.42 | 2924496 | 179 | 166
Dresden (B)-Dresden 345 kV | COMED_P1-2_345-L10805_B-S_SRT-A | COMED | COMED | 345 | 138 | 1524624.71 | 2831147.5 | 22 | 34
TSS 984 Crete EC-Saint John 345 kV | AEP_P1-2_#695_1681 | COMED | NIPS | 345 | 345 | 861102.51 | 2208673.5 | 48 | 76
Frostburg-Ridgeley 138 kV | AP-P1-2-PE-500-004 | APS | APS | 138 | 138 | 1649461.49 | 2183231.64 | 155 | 152
Shade Gap-Roxbury 115 kV | PECO_P1-2_5012_SRT-A/* $ CHESCO $ PECO_P1-2_5012 | PENELEC | PENELEC | 115 | 115 | 645889.19 | 2052018.67 | 59 | 132
North Waverly-E Sayre 115 kV | PN_P1-2_PN-230-101T_SRT-A | NYZC | PENELEC | 115 | 115 | 1644639.72 | 1970507.65 | 1347 | 1491
AC1-083 TAP-Smith Mountain 138 kV | AEP_P1-2_#311_5_SRT-A | AEP | AEP | 138 | 138 | 1541021.27 | 1964534.46 | 79 | 93
Kewanee-Putnam 138 kV | EXT_348921 4PRINCETN TP 138 348923 4EKEWANEE N 1 | COMED | AMIL | 138 | 138 | 876203.32 | 1537259.41 | 22 | 36
Bennett-Milford 230 kV | DPL_P1_2_CKT 23034 | DPL | DPL | 230 | 230 | 1193720.28 | 1336537.07 | 8 | 8
Southwest Lima-West Moulton 138 kV | AEP_P1-2_#14717_SRT-A | AEP | AEP | 138 | 138 | 1014817.63 | 1235020.12 | 36 | 56
Sedge Hill-Person 230 kV | DVP_P1-2: LN 570 | DOM | CPLE | 230 | 230 | 774123.06 | 1189140.31 | 52 | 86
Mahans Lane-TIDD 3-4 138KV BUS 138 kV | FE-P1-2-MP-138-556T | APS | AEP | 138 | 138 | 395362.36 | 998532.1 | 115 | 158
Crescent Ridge (R)-Corbin 138 kV | EXT_348921 4PRINCETN TP 138 348923 4EKEWANEE N 1 | COMED | AMIL | 138 | 138 | 854920.76 | 980214.91 | 68 | 68
Shade Gap-Roxbury 115 kV | AP-P1-2-PE-500-004 | PENELEC | PENELEC | 115 | 115 | 65329.39 | 947181.05 | 7 | 75
Juniata-Juniata 500 kV | PL:10:P13:100596 | PLGRP | PLGRP | 500 | 230 | 1530894.12 | 880802.56 | 45 | 8
E Towanda-Hillside PAR 230 kV | BASE CASE | PENELEC | NYZK | 230 | 230 | 690824.66 | 829066.3 | 1320 | 1607
Jct.-French's Mill 138 kV | BASE CASE | APS | APS | 138 | 138 | 1802219.68 | 823019.47 | 70 | 36
KYGER CREEK-SPORN 345 kV | BASE CASE | OVEC | AEP | 345 | 345 | 99355.87 | 766703.74 | 44 | 116
Dickerson-H-Dickerson 230 kV | AP-P1-2-PE-500-407T | PEPCO | PEPCO | 230 | 230 | 24261.94 | 758583.19 | 7 | 49
AXTON-AXTON 138 kV | AEP_P1-2_#311_5_SRT-A | AEP | AEP | 138 | 138 | 462416.18 | 710748.32 | 53 | 27
Terminal 2-Terminal 1 138 kV | DEOK_P1_TERMINAL 345/138 TB12 | DEOK | DEOK | 138 | 69 | 0 | 710703.06 | 0 | 1
E Frankfort (B)-TSS 984 Crete EC 345 kV | AEP_P1-2_#695_1681 | COMED | COMED | 345 | 345 | 468208.38 | 700941.39 | 27 | 24
Shade Gap-Roxbury 115 kV | BASE CASE | PENELEC | PENELEC | 115 | 115 | 10999.88 | 657601.81 | 4 | 73
Barracks Rd-Crozet 230 kV | DVP_P1-2: LN 291_SRT-A | DOM | DOM | 230 | 230 | 1004777.36 | 645140.71 | 10 | 21
Ashtabula 1-Sanborn Q-1 138 kV | ATSI_P1-2_CEI-345-720_SRT-A | FE-ATSI | FE-ATSI | 138 | 138 | 705766.64 | 628257.99 | 439 | 247
Crescent Ridge (R)-Corbin 138 kV Bus 1 138 kV | COMED_P1-2_138-L7413__R-S | COMED | AMIL | 138 | 138 | 553310.73 | 583132.98 | 98 | 94
Goose Creek 500/230 kV | DVP_P1-2: LN 595_SRT-A | DOM | DOM | 500 | 230 | 0 | 553073.19 | 0 | 1
Sedge Hill-Person 230 kV | DVP_P1-2: LN 570 | DOM | DOM | 230 | 230 | 329691.33 | 545899.3 | 24 | 40
Clubhouse 115 kV 1-Clubhouse 230 kV 115 kV | DVP_P1-2: LN 2201 | DOM | DOM | 115 | 230 | 518577.5 | 534849.16 | 34 | 37
Bremo 230 kV-Bremo 115 kV 230 kV | DVP_P1-2: LN 2193 | DOM | DOM | 230 | 115 | 147967.64 | 531972.19 | 27 | 60
ESS H447 Ritchie Road - Rochelle (R)-Rochelle - Caron Road 138 kV | COMED_P1-2_138-L16914_R-R_SRT-A | COMED | COMED | 138 | 138 | 419083.35 | 525462.33 | 90 | 72
Powerton-Towerline 138 kV | Fargo-Sandburg 345 kV | COMED | AMIL | 138 | 138 | 973455.08 | 485573.35 | 60 | 36
E Sayre-North Waverly 115 kV | PL_02_P12_000193_SRT-A | PENELEC | NYZC | 115 | 115 | 403546.32 | 457183.18 | 1792 | 1791
50045005 Interface | VINCO-HUNT |  |  |  |  | 0 | 426616.72 | 0 | 21
NW 2326&2322-Conastone 230 kV | PJM_500_BG_P1_5011_SRT-A | BGE | BGE | 230 | 230 | 544003.21 | 426168.97 | 7 | 11
Cartanza-Milford 230 kV | CKT 23030B | DPL | DPL | 230 | 230 | 285402.46 | 403550.87 | 21 | 31
Lallendorf-Monroe 1&2 345 kV | ATSI-P1-2-TE-345-605T | FE-ATSI | DECO | 345 | 345 | 435984.94 | 341770.42 | 98 | 44
Shade Gap-Roxbury 115 kV | PECO_P1-2_5012_SRT-A/* $ CHESCO $ PECO_P1-2_5012 | PENELEC | PENELEC | 115 | 115 | 18699.51 | 340417.22 | 5 | 10
Shade Gap-Roxbury 115 kV | PN-P1-2-PN-230-103AT | PENELEC | PENELEC | 115 | 115 | 1193.7 | 337729.4 | 3 | 52
Charlottesville 230 kV-Proffit Rd Del Pt 230 kV 230 kV | DVP_P1-2: LN 534 | DOM | DOM | 230 | 230 | 187418.13 | 317321.46 | 8 | 11
Mitchell-Wilson 138 kV | AEP_P1-2_#8598_552 | APS | DUQ | 138 | 138 | 41841.21 | 286052.12 | 1 | 2
Devon (R)-Rosehill Tap (R) 138 kV | COMED_P1-2_138-L11416_R-C_SRT-A | COMED | COMED | 138 | 138 | 209466.49 | 272362.05 | 2819 | 2811
DANVILLE 2-EAST DANVILLE 1 138 kV | BASE CASE | AEP | AEP | 138 | 138 | 69859.84 | 267650.64 | 9 | 20
Elwood (B)-Goodings Gr(B) 345 kV | COMED_P1-2_345-L11622_R-S_SRT-A | COMED | COMED | 345 | 345 | 89539.18 | 252432.25 | 18 | 21
Hosensack-Elroy 500 kV | E:501 ALBURTIS 500-BRANCHBG 500 (PLGRP-PSEG) [1] | PLGRP | PECO | 500 | 500 | 0 | 226481.45 | 0 | 2
Clybourn (B)-Diversey Tss 40 (B) 138 kV | BASE CASE | COMED | COMED | 138 | 138 | 172117.71 | 220508.97 | 5132 | 5587
Three Mile Island-Three Mile Island 500 kV | PECO_P1-2_5012_SRT-A/* $ CHESCO $ PECO_P1-2_5012 | METED | METED | 500 | 230 | 1596345.1 | 210174.84 | 35 | 5
Dickerson-Edwards Ferry 230 kV 230 kV | AP-P1-2-PE-500-407T | PEPCO | DOM | 230 | 230 | 0 | 185985.36 | 0 | 13
LEESVILLE-Altavista 138 kV 138 kV | BASE CASE | AEP | DOM | 138 | 138 | 227354.26 | 180347.2 | 5 | 4
Des Plaines Inductor-Higgins (B) 138 kV | BASE CASE | COMED | COMED | 138 | 138 | 128731.7 | 161562.56 | 2528 | 2450
KYGER CREEK-SPORN 345 kV | AEP_P1-2_#309_15_SRT-A | OVEC | AEP | 345 | 345 | 16485.5 | 155329.6 | 7 | 25
Glen Falls-Oakmound 138 kV | AP_P1-2_MP-138-013_SRT-A | APS | APS | 138 | 138 | 55598.82 | 154012.91 | 6 | 17
Yorkana-Brunner Island 230 kV | PECO_P1-2_5012_SRT-A/* $ CHESCO $ PECO_P1-2_5012 | METED | PLGRP | 230 | 230 | 0 | 149093.5 | 0 | 3
Crosby (R)-Diversey Tss 40 (R) 138 kV | COMED_P1-2_138-L14818_R-C | COMED | COMED | 138 | 138 | 103205.4 | 135329.34 | 4526 | 4998
Powerton (R)-false 345 kV | COMED_P1-2_345-L1202__B-S | COMED | AMIL | 345 | 345 | 68153.05 | 130764.05 | 1 | 2
Battleboro 115 kV-Rocky Mount 115 kV | DVP_P1-2: LN 2058_SRT-A | DOM | CPLE | 115 | 115 | 0 | 116736.02 | 0 | 6
Burches Hill-Palmers Corner 090 230 kV | PEPCO_P1_PP67 | PEPCO | PEPCO | 230 | 230 | 191518.74 | 111412.6 | 344 | 145
E Sayre-North Waverly 115 kV | PL_02_P12_000082_SRT-A | PENELEC | NYZC | 115 | 115 | 67533.77 | 110751.46 | 515 | 630
Garrett Tap-Garrett 115 kV | PN-P1-2-PN-115-068 | PENELEC | APS | 115 | 115 | 76452.86 | 105882.65 | 15 | 15
Barracks Rd 230 kV 1-Crozet 230 kV 2 230 kV | DVP_P1-2: LN 553 | DOM | DOM | 230 | 230 | 0 | 103176.12 | 0 | 4
NW 2326&2322-Conastone 230 kV | BG_P1_2310 | BGE | BGE | 230 | 230 | 133902.42 | 92803.86 | 6 | 4
Grenshaw (R)-Washington Park (R) 138 kV | BASE CASE | COMED | COMED | 138 | 138 | 49325.22 | 88689.35 | 4249 | 4680
Natoma (B)-Oak Park (B) 138 kV | BASE CASE | COMED | COMED | 138 | 138 | 70984.7 | 88684.71 | 3866 | 3825
Devon (B)-Rosehill Tap (B) 138 kV | BASE CASE | COMED | COMED | 138 | 138 | 45600.18 | 85149.86 | 352 | 456
Buzzard Point 138kV-Buzzard Point 026 138 kV | PEPCO_P1_PP73_SRT-A | PEPCO | PEPCO | 138 | 230 | 125056.9 | 82978.61 | 664 | 481
Cherry Run-Harmony Jct 138 kV | AP_P1-2_WP-138-110A_SRT-A | APS | APS | 138 | 138 | 0 | 81978.22 | 0 | 6
Face Rock-Five Forks 2-Face Rock-Five Forks 115 kV | BASE CASE | PLGRP | PLGRP | 115 | 69 | 197455.42 | 70077.36 | 10 | 4
Kewanee-Kewanee 138 kV | COMED_P1-2_138-L98105_R-S | COMED | COMED | 138 | 138 | 62841.27 | 62314.93 | 15 | 9
BENTON HARBOR-SEGRETO 345 kV | AEP_P1-2_#7023_8101690 | AEP | AEP | 345 | 345 | 0 | 59907.32 | 0 | 14
ARGENTUM SUBSTATION 69 KV BUS-GRAYS BRANCH 69 kV | AEP_P2-1_243688 05S.PORT MTR 138 342538 4ARGENTU | EKPC | AEP | 69 | 69 | 47687.74 | 58822.64 | 11 | 13
Nottingham-Nottingham Reactor bus on Line 220-08 230 kV | PECO_P1-2_5012_SRT-A/* $ CHESCO $ PECO_P1-2_5012 | PECO | PECO | 230 | 230 | 119727.64 | 54940.84 | 23 | 1
Germantown-Straban 115 kV | ME_P1-2_ME-500-004T_SRT-A | METED | METED | 115 | 115 | 0 | 53422.14 | 0 | 3
Central Interface | WESCO-SUSQ |  |  |  |  | 596.32 | 53412.06 | 1 | 4
Shade Gap-Roxbury 115 kV | PN-P1-2-PN-230-103AT | PENELEC | PENELEC | 115 | 115 | 0 | 46644.07 | 0 | 7
Johnstown-Bear Rock 230 kV | BASE CASE | PENELEC | PENELEC | 230 | 230 | 0 | 42978.67 | 0 | 2
Trade City-Dixonville East 115 kV | AP_P1-2_WP-345-311T_SRT-A | PENELEC | PENELEC | 115 | 115 | 0 | 41651.19 | 0 | 4
CLIFTY CREEK-Carrollton 138 kV | EXT_249532 08TRIMBL 345 324105 7GHENT 345 1 | OVEC | LKE | 138 | 138 | 0 | 41395.64 | 0 | 2
PPL-BGE Tie Bus-Graceton 230 kV | PL_04_P12_000260_SRT-A | PLGRP | BGE | 230 | 230 | 31166.94 | 32282 | 10 | 11
Stanley Terrance Bus Section 2-McCarter 230 kV | PS_P1-2_A-2306 | PSEG | PSEG | 230 | 230 | 25797.01 | 31924.45 | 2350 | 3261
State Line (B)-Roxana 138 kV | EXT_P12:345:NIPS:34520:17SHEFFIELD:17GARY_AVE:1 | COMED | NIPS | 138 | 138 | 1215.24 | 30396.35 | 9 | 45
Grenshaw (B)-Taylor (B) 138 kV | BASE CASE | COMED | COMED | 138 | 138 | 17031.99 | 28670.18 | 1154 | 1168
Washington Park (B)-State Line Phase Shifter State Line-Washington Pa 138 kV | COMED_P1-2_138-L17008_B-C_SRT-A | COMED | COMED | 138 | 138 | 31176.01 | 27539.06 | 1511 | 1628
All Dam 6 Tap-Kittanning 138 kV | AP_P1-2_WP-345-311T_SRT-A | APS | APS | 138 | 138 | 20929.46 | 27293.53 | 8 | 4
Grenshaw (B)-University (B) 138 kV | COMED_P1-2_345-L17705_B-S | COMED | COMED | 138 | 138 | 9885.27 | 27135.79 | 96 | 107
Crawford (G)-Crawford PAR 138 kV | BASE CASE | COMED | COMED | 138 | 138 | 16748.29 | 25555.87 | 2420 | 2439
Northwest PAR-Northwest (R) 138 kV | BASE CASE | COMED | COMED | 138 | 138 | 13431.04 | 24013.55 | 514 | 555
E Sayre-North Waverly 115 kV | PN_P1-2_PN-345-104T_SRT-A | PENELEC | NYZC | 115 | 115 | 446.25 | 22686.97 | 40 | 115
Crawford (Y)-Crawford PAR 138 kV | BASE CASE | COMED | COMED | 138 | 138 | 12719.92 | 20692.19 | 1473 | 1619
Ridgeland (B)-Ridgeland PAR 138 kV | BASE CASE | COMED | COMED | 138 | 138 | 9713.12 | 16221.77 | 972 | 1441
Meadow Brook-Strasburg 138 kV | DVP_P1-2: LN 550 | APS | APS | 138 | 138 | 0 | 15584.82 | 0 | 2
All Dam 6 Tap-Kittanning 138 kV | AP_P1-2_WP-138-085A_SRT-A | APS | APS | 138 | 138 | 48211.06 | 13912.04 | 21 | 19
KYGER CREEK-SPORN 345 kV | AEP_P1-2_#7441_100545_SRT-A | OVEC | AEP | 345 | 345 | 0 | 13526.15 | 0 | 1
Franklin Park (R)-Franklin Park PAR (R) 138 kV | BASE CASE | COMED | COMED | 138 | 138 | 10832.69 | 13459.32 | 1236 | 1768
State Line Phase Shifter State Line-Washington Pa-Washington Park (B) 138 kV | COMED_P1-2_138-L0708__B-C_SRT-A | COMED | COMED | 138 | 138 | 9774.35 | 12436.84 | 615 | 718
Crawford (R)-West Loop (R) 345 kV | COMED_P1-2_345-L1310__B-C | COMED | COMED | 345 | 345 | 14819.4 | 12270.59 | 174 | 261
Crosby (B)-Rockwell (B) 138 kV | BASE CASE | COMED | COMED | 138 | 138 | 10132.42 | 11605.44 | 569 | 978
Higgins (B)-Natoma (B) 138 kV | BASE CASE | COMED | COMED | 138 | 138 | 4994.1 | 11109.03 | 365 | 586
All Dam 6 Tap-Kittanning 138 kV | PN_P1-2_PN-345-107T_SRT-A | APS | APS | 138 | 138 | 99689.79 | 10945.73 | 81 | 4
*Current work-in-progress modeling items not finalized yet include but are not limited to the following: Joliet retirement announcement. Dominion’s immediate need solution to Data Center Alley area. PV transfer analysis to determine the reactive limits for the PJM interfaces. Improved modeling detail and any corrections received as part of the model review process. Interregional updates.