## Setup
Enter Stakeholder Committee Name in cell A2:
Interconnection Process Subcommittee
Enter issue title (use title from Issue Tracking if applicable) in cell A5:
Capacity Interconnection Rights (CIR) Transfer Efficiency

## 1. Interest Identification
Interconnection Process Subcommittee
Capacity Interconnection Rights (CIR) Transfer Efficiency
Interest Identification
Instructions: List interests of all parties on this page.
1 | Allow for an efficient and timely process to minimize diverting resources away from cluster interconnection request studies
2 | Ensure no discriminatory impacts to other interconnection processes
3 | Ensure system capability is being utilized and granted equitably
4 | Establish a clear queue priority among Replacement Generation requests
5 | Minimize impacts to existing rules and requirements associated with Deactivation resources/process
6 | Maintain site control requirements for Replacement resource
7 | Ensure PJM system reliability and scope of reliability studies is not degraded
8 | Ensure Affected System coordination is maintained for Affected System reliability
9 | Clearly address what to do with the existing Replacement Gen requests
10 | Transparent and nondiscriminatory
11 | Open to all current and future Interconnection Customers
12 | Replace all, or a portion of, an Existing Generating Facility with a newer and more efficient Generating Facility
13 | Apply “First Ready, First Served” principals to Replacement Generation requests
14 | Minimize study requirements for Replacement Generation
15 | Minimize financial security requirements for Replacement Generation requests.
16 | Allow interconnection requests with the same POI to be segmented by time
17 | Allow interconnection requests with the same POI to be segmented by developer
18 | Retain the ability for interconnection requests with the same POI to be segmented by technology
19 | Allow interconnection requests with the same POI to mix and match segmentation by time, developer, and technology
20 | Ensure no discriminatory impacts to projects currently in the queue, specifically in regard to queue priority and network upgrade cost allocations
21 | Allow exisiting generators to replace retiring resources with any and all fuel sources and technologies. For example thermal resources to battery storage.
22 | No unnecessary delays in bringing new resources online to ensure resource adequacy
23

## 2. Options Matrix- Design Comp.
Interconnection Process Subcommittee
Capacity Interconnection Rights (CIR) Transfer Efficiency
OPTIONS MATRIX
Solution Options2
# | Design Components1 | Priority | Status Quo | A | B | C | D | E | F | G | H | I
* | Implementation
1 | Eligible deactivating resources |  | All resources provided that the resource has CIRs (i.e. Generation Capacity Resources) & the resource has submitted an official deactivation notice to PJM | A: All resources provided that the resource has CIRs (i.e. Generation Capacity Resources) and the resource has submitted a deactivation notice to PJM or submitted to PJM a notification of anticipated date range of deactivation of the resource. | Color Key: PJM Comments, PJM New, AEP, MMU, Elevate, Gabel Associates
2 | Eligible replacement resources |  | All resources including storage devices provided that the resource has requested CIRs with their New Serivce Request application (i.e. requested to be a Generation Capacity Resource) | A: All resources including storage devices provided that the resource has requested CIRs with their generator replacement application (i.e. requested to be a Generation Capacity Resource); B: All Resources, including Storage Devices, provided that the existing generating resource has CIRs and has submitted to PJM a deactivation notice or notification of the anticipated date range of deactivation.
3 | Criteria for determining a transfer under this process is permissible |  | All generation resources provided that the resources have CIRs (i.e. Generation Capacity Resource). The same CIR holder for both the deactivation resource and the replacement resource. A deactivation notice submitted to PJM. Submission of a new service request application and notice to intent to transfer CIRs form prior to CIRs expiring. | All generation resources, including energy storage, provided that the resources have CIRs (i.e. Generation Capacity Resource). The same CIR holder for both the deactivation resource and the replacement resource. A deactivation notice submitted to PJM or notification of anticipated date range of retirement submitted to PJM. Expedited evaluation of generator retire-replacement ("Generator Retirement Process") via a stand alone process outside of PJM's New Service Request Process. | All generation resources, including Battery Storage fuel type, provided that the resources have CIRs (i.e. Generation Capacity Resource). The same CIR holder for both the deactivation resource and the replacement resource. A deactivation notice submitted to PJM. Submission of a replacement resource application and notice of intent to transfer CIRs form prior to CIRs expiring. | All generation resources, including energy storage, provided that the resources have CIRs. Expedited evaluation of generator retire-replacement via a stand alone Generation Facility Replacement process outside of PJM's New Service Request Process. | All resources provided that the resource has CIRs (i.e. Generation Capacity Resources) & the resource has submitted an official deactivation notice to PJM. The result is not a bilateral transfer but a return of the CIRs to the grid to increase headroom for the next resource(s) in the queue. | All Resources, including Storage Devices, provided that the existing generating resource has CIRs and has submitted to PJM a deactivation notice or notification of the anticipated date range of deactivation. A notice of intent to transfer CIRs must be submitted before they expire. This process will occur as a stand-alone process outside of the current new interconnection services agreement process, i.e. new generator replacement process. | Proposal for status quo: i) A deactivation notice for the existing resource submitted by the current CIR holder, ii) A new service request for the replacement resource submitted by the proposed transferee of the CIRs, iii) notice of intent to transfer CIRs from the current holder to the transferee (which may be the same entity or another one)
4 | New/Modified Definitions (i.e. Material Modification) |  | Material Modification OATT Part VIII, Subpart A, section 400 Definitions “Material Modification” shall mean, as determined through a Necessary Study, any modification to a Generation Interconnection Agreement that has a material adverse effect on the cost or timing of Interconnection Studies related to, or any Distribution Upgrades, Network Upgrades, Stand Alone Network Upgrades or Transmission Owner Interconnection Facilities needed to accommodate, any Interconnection Request with a later Cycle. | A: Material Modification shall mean (1) modification to an Interconnection Request in the queue that has a material adverse impact on the cost or timing of any other Interconnection Request with a later queue priority date unless willing to be mitigated by the modifying facility; or (2) planned modification to an Existing generating facility that is undergoing evaluation for a generating facility modification or generating gacility replacement, and has a material adverse impact on the Transmission System with respect to: i) steady-state thermal or voltage limits, ii) dynamic system stability and response, or iii) short-circuit capability limit; compared to the impacts of the existing generating facility prior to the modification or replacement. The addition of a generating facility, for example, an energy storage resource addition, to a pending interconnection request or planned modification to an existing generating facility that is undergoing evaluation for a generating gacility modification or generating facility replacement, will not automatically be deemed a material modification. PJM Comment: if a Solution Option would like to modify the PJM OATT "Material Modification" definition to address this Issue Charge topic, at a minimum, it should inlcude the existing definition as the existing definition (see Status Quo) is presently geared towards the PJM Cycle Process/interconnection projects, which needs to remain unchanged for projects in the Cycle Process.; B: New/Modified Definitions (i.e. Material Modifcation) PJM Comment: recommend deleting. This cell is re-stating the Design Component.; C: The term and application of "Material Modification" are not applicable to this process. "Material Adverse Impact" is the appropriate measure under the new generator replacement process. (Remove Design Component 4) PJM Tariff Definitions, Attachment P, Appendix 2, section 3.4.l. (Material Modification) OATT Part VIII, Subpart A, section 400 Definitions
5 | Public Posting of Replacement Generation Requests |  | CIR transfers to replacement resources are assigned a PJM project identifier within the PJM New Service Request process and posted to the PJM New Service Request webpage | A: Additonal language to existing defintion/requirements pertaining to Generating Facility Replacement Requests; "for a Generating Facility Replacement, the planned date of cessation of operation for the Existing Generating Facility, notification of anticipated date range of retirement submitted to PJM or actual date if the Existing Generating Facility already has ceased commercial operations, the expected Commercial Operation Date of the replacement facility and requested Interconnection Service."; B: Post all Replacement Generation Requests on a new PJM Replacement Generation webpage. Include details of the new Replacement Resource similar to the details posted for new Generation Interconnection projects in the Cycle Process (Project Name/POI, State, TO, MFO, MWE, MWC, Fuel, Application Submittal Date, Requested Commercial Operation Date, Status, etc). Include the Deactivation unit(s) whose CIRs are being claimed by the Replacement Resource, the amount of CIRs being claimed, as well as the Projected or Acutal Deactivation Date.; C: CIR availability posted publicly at the time of the deactivation notice and effective on the deactivation date.; D: CIR transfers to replacement resources posted on a new PJM Replacement Generation webpage, which would include details of the new Replacement Resource similar to the details posted for new Generation Interconnection projects in the Cycle Process (Project Name/POI, State, TO, MFO, MWE, MWC, Fuel, Application Submittal Date, Requested Commercial Operation Date, Status, etc). Include the Deactivation unit(s) whose CIRs are being claimed by the Replacement Resource, the amount of CIRs being claimed, as well as the Projected or Acutal Deactivation Date.
6 | POI Requirements of Replacement Resource |  | Replacement generation resource is not required to be located at the same Point of Interconnection (POI) as the Deactivation generation resource | A: Any Replacement Generating Facility must connect to the Transmission System at the same or electrically equivalent Point of Interconnection (i.e. same voltage level at the interconnecting substation) as the Existing Generating Facility. PJM: This Solution Option is Pending the determination of in/out of scope of the Issue Charge. Issue Charge states different POIs are out of scope.; B: Replacement Resource must connect at the same POI. POI is defined per OATT Part VIII as the point or points where the Interconnection Facilities connect with the Transmission System. Replacement Resource must utilize the same electrical node (i.e. breaker position) as the Deactivation Resource.; C: Replacement generation resource is not required to be located at the same Point of Interconnection (POI) as the Deactivation generation resource. If interconnecting to same POI or different breakers within the same substation, expedited evaluation of generator retire-replacement via a stand alone Generation Facility Replacement process outside of PJM's New Service Request Process. PJM Comment: suggest adding for clarity that Replacement generation resources at different POIs will continue to be processed in PJM's Cycle Process along with all other interconnection requests. This Solution Option is Pending the determination of in/out of scope of the Issue Charge. Issue Charge states different POIs are out of scope.; D: Use of CIRs by new resources defined by standard PJM planning criteria. POI requirements for replacement resources should be per existing tariff.; E: Replacement resource to be located at the same Point of Interconnection (POI) as the Deactivation generation resource ("Same" term used for administrative ease not technical determination in the IC/PS); POI considered "point or points" including different breakers within the same substation or within 1 mile where the Interconnection Facilities connect with the Transmission System. PJM: This Solution Option is Pending the determination of in/out of scope of the Issue Charge. Issue Charge states different POIs are out of scope.
7 | MW Requirements of Replacement Resource |  | The holder of the CIRs will retain only such rights that are commensurate with the size in megawatts of the replacement generation, not to exceed the amount of the holder’s Capacity Interconnection Rights associated with the facility upon Deactivation or removal of Capacity Resource status. The replacement gen request has no upper limit on the CIRs, nor the MFO they are requesting with their generation interconnection New Service Request. | A: Requesting CIRs equal to or less than those of retiring generator; B: Replacement Resource must request a CIR value less than or equal to the CIR value of the Deactivation Resource. Replacement Resource must request a MFO value less than or equal to the MFO value of the Deactivation Resource.; C: The new holder of the CIRs will receive CIRs based on the ICAP value of the new resource. The replacement gen request has no upper limit on the CIRs they are requesting.; D: The transfer amount of CIRs to the replacement resource must be less than or equal to the CIRs associated with the deactivating resource.
8 | Initiation of CIR Transfer Process |  | The same CIR holder for deactivation resource and replacement resource. Requirement of a deactivation notice to PJM. Once a deactivation notice has been received by PJM, Submission of new service request application and notice of intent to transfer CIRs form prior to CIRs expiring, which is 1 year after the Actual Deactivation Date. | The request for Generating Facility Replacement must be submitted at least one (1) year prior to the date that the Existing Generating Facility will cease operation unless the Existing Generating Facility is in suspension or in Forced Outage, and must include the planned date of cessation of operation for the Existing Generating Facility or anticipated date range of planned cessation of opeation and the expected Commercial Operation Date for the Replacement Generating Facility. An Interconnection Customer (IC) shall submit to PJM a Generating Facility Replacement request by providing an executed study agreement and the deposit. | Submission of deactivation notice and intent to transfer CIRs form – publicly posted on generation owner and PJM websites PJM Comment: public posting topic is a separate Design Component #5 | A deactivation notice submitted to PJM. The same CIR holder for both the deactivation resource and the replacement resource. Once a deactivation notice has been received by PJM, submission of a Replacement Resource application and notice of intent to transfer CIRs form prior to CIRs expiring. | As soon as a generator gives notice of deactivation to PJM, it can designate a replacement generator to claim its CIRs. CIRs must be claimed by another generator prior to the closing of the next study cycle in the standard interconnection queue process. Replacement generator must meet the criteria for transfer (i.e., cannot increase MFO or CIR requirement, as specified in Item 7). | Can have different ownership but only if it is an Affiliate or business partner of the owner of the Deactivation Resource. Submission of Generation Facility Replacement application and notice of intent to transfer CIRs form prior to CIRs expiring, which is 1 year after the Actual Deactivation Date. | The next resource in the queue that can use CIRs from the deactivating unit will have first call on the released CIRs, if it is active status and ready to proceed to commercial operation within 12 months. | CIR Transfer for Existing Generator/Generation Replacement process commences with (1) request submitted at least one (1) year prior to the date that the Existing Generating Resource will cease operation unless the Existing Generating Resource is in suspension or in Forced Outage, (2) request must include the planned date of cessation of operation for the Existing Generating Resource or anticipated date range of planned cessation of operation for the Existing Generating Resource; and (3) the expected Commercial Operation Date for the Replacement Generating Resource. | Initiation of CIR Transfer can be made by any Generator so long the Deactivating Generator has submitted a Deactivation Notice sent to PJM and the via submission of “Notice of Intent to Transfer CIRs” form has been submitted within 1 year of the actual Deactivation Date. Notice of intent to capture the transfer and/or selling of the CIR's to the new holder. Consistent with existing Manual 14G, §4.4.1.2 | Submission of a generator replacement request (and potentially a CIR transfer notice/agreement if that's part of the replacement process). | Low
9 | Commercial Operation date of replacement generation |  | As determined in the GIA. | No more than three (3) years from the date of execution of the GIA or four (4) years from the date a unit is determined to be in forced outage. If the requested period of time between the cessation of operation of the Existing Generating Facility and expected Commercial Operation Date of the Replacement Generating Facility is more than three (3) years from the execution of the GIA, the request shall be treated as Interconnection request for a new Generating Facility. | In general, same Commercial Operation date requirements as new generation interconnection requests in the Cycle Process. One specific requirement would be that the Replacement Resource cannot commercially operate prior to the Actual Deactivation Date of the Deactivation Resource (system has not been evaluated to allow operation of both resources simultaneously). | A GIA for replacement generation can be executed after completion of the Generation Facility Replacement study process, including anytime prior to the deactivation date of the retiring facility, but in no case may the Commercial Operation Date of the Replacement Generating Facility occur prior to the deactivation date of the retiring facility. The Commercial Operation Date of the Replacement Generating Facility may be no more than three (3) years from the date of execution of the GIA, with such time to be extended to allow for decommissioning of the deactivated resource, not to exceed a total of (6) years from GIA execution. The time needed for decommissioning shall be measured from the date the deactivated resource is deactivated until it is decommissioned. | Replacement generation must commit to commercial date within 12 months of CIR transfer. | The Commercial Operation Date of the Replacement Generating Resource may occur prior to the deactivation date of the retiring Generating Resource, but the Commercial Operation Date of the Replacement Generating Resource may be no more than three (3) years from the date of execution of the GIA. If the requested period of time between the cessation of operation of the Existing Generating Resource and the expected Commercial Operation Date of the Replacement Generating Resource is more than three (3) years from the execution of the GIA, without waiver for extension granted, the request shall be treated as an Interconnection request for a new Generating Facility. | "COD of replacement resource would be expected to occur within 3 years of initiation of generator replacement process. Requests for extension would be reviewed case by case by an appropriate auditor." |  |  |  | Low - Medium
10 | Priority among Replacement Resource requests |  | The Replacement generation resource, along with the CIR Transfer, is evaluated and processed as part of the PJM New Services Request Process. | A: The Replacement generation resource, along with the CIR Transfer, is evaluated and processed in the order in which they are submitted.; B: Replacement Resource requests prioritized serially, in the order in which the Replacement Resource request is received by PJM. Each Replacement Resource request to be assigned a Replacement Resource request Number.; C: Replacement Resource requests are processed serially in the order in which the Generation Facility Replacement application is received by PJM. Each Replacement Resource will be assigned a Generation Facility Replacement application number. PJM Comment: same as Solution Option B but with slightly different terminology.; D: Priority will depend on whether the new resource solves reliability issues that would otherwise require an RMR.; E: The replacement resource, along with the CIRs of the deactivating resource, will be evaluated and processed in 180 days through a stand-alone process outside of the current new interconnection services agreement process, i.e. new generator replacement process. The replacement resource requests will be processed in the order the requests are received by PJM. | Low - High
11 | Screening criteria, Study Phases, and scope of each Study Phase (More Detailed Description added in tab 2a of Matrix for additional clarity considerations) The screening criteria includes an assessment of whether the replacement resource would trigger network upgrades |  | Transfers of CIRs are evaluated through System Impact Studies (Phases 1-3 of Cycle Process) performed by PJM (including load flow, short circuit and stability). | The evaluation will consist of two studies: i) a Replacement Impact Study and ii) a Reliability Assessment Study. PJM shall use Reasonable Efforts to complete the Replacement Impact Study and Reliability Assessment Study and share results with the IC within one hundred eighty (180) Calendar Days of the request. PJM Comment: this seems to reflect the MISO Replacement Gen Process. Note the 2nd study noted here (ii) "Reliability Assessment Study" in MISO is a study that evalautes the system without the Deactivating unit nor the Replacement Gen unit (for the timeframe between the deactivation date and the commercial operation date of the Replacmeent unit)(see MISO BPM-015). This study in PJM is the Deactivation Study as covered under PJM OATT Part V Deactivation Process and likely not in scope to be changed with this Issue Charge. | Network upgrades are allowed | A process for cost allocation for any network upgrades. PJM Comment: this may already be captured as Design Component #21. | Application Phase (ensure Application requirements met, deficiency review, kickoff/scoping call) Impact Study Phase (can include intitial screening assessment if needed, run all required reliability analyses) Facilities Study Phase (if any of these needed)(if new interconnection facilities, metering/relaying, new network upgrades) Final Agreement Negotiation Phase (draft GIA for Project Developer, TO, PJM execution)(provide security) | The System Impact Study portion of the expedited Generation Facility Replacement study process will consist of two studies: i) a Replacement Impact Study (RIS) and ii) a Reliability Assessment Study (RAS). PJM shall complete the Replacement Impact Study and Reliability Assessment Study and share results with the IC within one hundred eighty (180) Calendar Days of the request. PJM Comment: this seems to reflect the MISO Replacemetn Gen Process. Note the 2nd study noted here (ii) "Reliability Assessment Study" in MISO is a study that evalautes the system without the Deactivating unit nor the Replacement Gen unit (for the timeframe between the deactivation date and the commercial operation date of the Replacmeent unit)(see MISO BPM-015). This study in PJM is the Deactivation Study as covered under PJM OATT Part V Deactivation Process and likely not in scope to be changed with this Issue Charge. Because a Deactivation Resource paid for Network Upgrades at the time it originally entered service, no additional Network Upgrades will be assigned to the Replacement Resource, provided CIRs transferred are equal to or less than the Deactivation Resource, and Replacement Resource is able to mitigate NUs associated with short circuit and related study results. PJM Comment: network upgrades could be assigned to the Replacement Resource due to non-CIR related issues such as energy-only MWs and different fuel types due to PJM Deliverability rules as covered in IPS PJM Training. | The new generator replacement process, including Transfers of CIRs, are evaluated through a Stability and Short Circuit Study. Network upgrades are allowed if issues are identified and the replacement generator can enhance the generating facility or the interconnecting substation to address the issues. PJM shall use reasonable effort to complete the Stability and Short Circuit Study and share the results with the IC within one hundred eighty (180) calendar days of the request. | Application Phase (ensure Application requirements met, deficiency review, kickoff/scoping call) Combined Impact Study/Facilities Study Phase (can include intitial screening assessment if needed, run all required reliability analyses) (if any of these needed)(if new interconnection facilities, metering/relaying, new network upgrades) Final Agreement Negotiation Phase (draft GIA for Project Developer, TO, PJM execution)(provide security) | The replacement resource, along with the CIRs of the deactivating resource, will be evaluated and processed within 180 days through a stand-alone process outside of the current new interconnection services process, i.e. new generator replacement process. | The generator replacement process will be evaluated through a stand-alone process that is not subject to the conventional interconnection queue process timeline and with limited studies limited to determining the impact of differences between the Deactivating Generator and Replacement Generator. If PJM/TOs perform the studies, PJM to share the results of the study within 120 days. PJM to allow the use of pre-approved consultants for expedited study and will provide a determination on the provided results. PJM/TOs to provide their review of the results and the determination on the results of the studies within 60-days of delivery of the results (open to a different timeline). Use of pre-approved consultants removes liability for study delays past the 120-days. | Medium
12 | Replacement Resource Facilities Study |  | Facilities Studies are performed during the Cycle Process. In Phase 2, the Facilities Study for Interconnection Facilities is done (if required). In Phase 3, the Facilities Study for Network Upgrades is done (if required). | A: If PJM determines such a study is necessary, upon IC’s notice to proceed to PJM after completion of the RIS and the RAS. This Interconnection Facilities Study will identify estimates for cost and the time required to construct the Interconnection Facilities. PJM shall use Reasonable Efforts to complete this portion of the Interconnection Facilities Study within ninety (90) Calendar Days.; B: Facilities Study (if any of these needed)(if new interconnection facilities, metering/relaying, new network upgrades) Develop cost and time estimates for such required work. Gen Replacement Process rules will dictate allowed scope based on POI Requirements/if new interconnection facilities are allowed, if new network upgrades are allowed, etc. The allowed scope may ultimately drives the target Facilities Study timeline.; C: The Facilities Study portion of the expedited Generation Facility Replacement study process will identify estimates for cost and the time required to construct the Interconnection Facilities. PJM shall complete this portion of the Interconnection Facilities Study within ninety (90) Calendar Days.; D: The new generator replacement process, including Transfers of CIRs, are evaluated through a Stability and Short Circuit Study. Network upgrades are allowed If issues are identified and the replacement generator can enhance the generating facility or the interconnecting substation to address the issues. PJM shall use reasonable effort to complete the Stability and Short Circuit Study and share the results with the IC within one hundred eighty (180) calendar days of the request.
13 | Criteria for Generator Replacement Requests that are found to have adverse impacts to transmission system |  | The Replacement generation resource is part of a Cycle within the PJM New Services Request Process and cost responsibility may be shared with other New Service Requests in the same Cycle, if impacts are found | A: If the removal of the existing generator would lead to material reliability issue on the grid, then PJM will address such issues as a regional reliability upgrade, and the Interconnection Request will be processed under the proposed Generator Replacement Rules. If a material impact is identified that is caused by the proposed new Generating Facility, the IC will be notified and provided an opportunity to modify its proposed facility to remove the adverse impact or to sponsor upgrades required to remove the adverse impact.; B: If the Replacement Resource is identified to be causing reliability criteria violations and requiring new Network Upgrades be constructed on the system, then the Replacement Resource request to be Withdrawn and can enter the Cycle Process to be evaluated and processed in the Cycle Process.; C: If the Replacement Resource degrades any thermal, short circuit, stability capability available on the system, as compared to the Deactivation Resource, will be deemed a "material adverse impact" to the system. The Replacement Resource would consume available transmsision capability (i.e. headroom) from the system in excess of what the Deactivation Resource already utilized. If this occurs, then the Replacement Resource request to be Withdrawn and can enter the Cycle Process to be evaluated and processed in the Cycle Process.; D: Request will be processed under the proposed expedited Generation Facility Replacement process. If the Replacement Generation MFO exceeds the Deactivation Resource MFO, and a material impact is identified, the IC will be notified and provided an opportunity to modify its proposed facility to remove the adverse impact or to sponsor upgrades required to remove the adverse impact.; E: 1.) If the removal of the Existing Generating Resource creates a material reliability issue on the grid, then PJM will address such issues as a regional reliability upgrade, and the generator replacement request will be processed under the proposed Generator Replacement Rules. 2.) If the new proposed Replacement Resource is deemed to cause an "adverse material impact," the IC will be notified and provided an opportunity to address any issues or to modify the proposed Replacement Resource to mitigate the "adverse material impact," or sponsor upgrades to remove the "adverse material impact." 3.) If the new proposed replacement resource causes an "adverse material impact," and the IC does not seek to modify or mitigate, then the replacement resource request will be deemed withdrawn, and the IC may enter the "New Service Request" process.
14 | Application and Deposit Requirements for Replacement Resource |  | Applicant must submit any claim from the deactivating generating units with their application, and it must be received by the Application Deadline. CIR claims must be submitted using the CIR Transfer template available on the PJM website. Deposit based on PJM's new process. | A: Deposit Requirement same as a generation interconnection request entering the Cycle Process (deposit increases with increased MFO request)(see M14H section 2.5.1); B: Deposit Requirement: $200K Based on PJM Cycle deposit requirement for generation interconnections as small as 20-50 MW (see M14H section 2.5.1). Ensure covers all reliability analyses including stability and TO Facilities Study if needed.; C: Applicant must submit any claim to CIRs of Deactivation Resource with its application into the expedited Generation Facility Replacement Study process. CIR claims must be submitted using the CIR Transfer template available on the PJM website. Deposit should be $60k consistent with MISO and SPP amount for replacement study processes.; D: 1.) Application: To initiate and establish a new generation replacement request, the replacement resource applicant will submit a replacement resource request; the existing generating resource has CIRs and has submitted to PJM a deactivation notice or notification of the anticipated date range of deactivation; A notice of intent to transfer CIRs has been submitted before they expire. 2.) Deposit: The replacement resource shall submit a deposit of $60,000. 3.) Consultant Fee: The replacement resource shall submit a deposit for third-party consulting assistance for PJM expedited study reviews to meet 180-day completion
15 | Decision Points during Study Process |  | There are decision points 1, 2, and 3 after Phases 1,2,3 of the Cycle Process. | A: IC requesting Generating Facility Replacement shall inform PJM within thirty (30) Calendar Days after having received results of the RIS and RAS of its election to proceed and PJM will initiate a Facilities Study or tender a draft GIA. Failure by the IC to provide an election to proceed within thirty (30) Calendar Days will result in withdrawal of the Interconnection Request; B: 30 day Decision Points after Impact Study Phase and Facilities Study Phase; C: IC requesting Generating Facility Replacement shall inform PJM within thirty (30) Calendar Days after having received results of the RIS and RAS of its election to proceed and PJM will initiate a Facilities Study or tender a draft GIA. Failure by the IC to provide an election to proceed within thirty (30) Calendar Days will result in withdrawal of the Replacement Request Replacement Resource requests to have the same site control requirements as new generation interconnection requests PJM New Services Request Process. However, the generation replacement process is a separate review process outside of PJM’s New Service Request process, as a result, decision points during the study process shouldn’t apply.; D: 1, 30 day Decision Point after Developer receives Impact Study and Facilities Study (if required). The Decision Point will run concurrently with a 60 day Final Agreement Negotiation Phase. 100% Security due at end of 30 day Decision Point. This Solution Option mimics the Decision Point/Final Agreement Negotiation Phase in the Cycle Process.
16 | GIA Requirements |  | GIA issued for Replacement resource as part of the New Services Request Process, per the OATT sections covering the New Services Request Process | A: PJM shall tender a draft GIA to the IC thirty (30) Calendar Days after the IC communicates its election to proceed with Generator Replacement if a Facilities Study is not required or within thirty (30) Calendar Days after final Facility Study reports are provided to the IC. The draft GIA shall include appendices describing the timing of Generating Facility Replacement and a condition that the GIA cannot be assigned and the Replacement Generating Facility cannot be transferred to any other Party, including an affiliate of the IC, until such date as the Replacement Generating Facility achieves commercial operation.; B: GIA Requirements similar to GIAs issued for Interconnection requests claiming CIRs in the Gen Interconnection Cycle Process; C: PJM shall tender a draft GIA to the IC thirty (30) Calendar Days after the IC communicates its election to proceed with Generator Replacement if a Facilities Study is not required or within thirty (30) Calendar Days after final Facility Study reports are provided to the IC.; D: PJM shall tender a draft pro forma amended GIA or GIAs within 30 Calendar Days following approval of Replacement Resource as part of the New Generation Replacement Resource process that occurs as a stand-alone process outside of the current new interconnection services agreement process, i.e. new generator replacement process.
17 | Site Control Requirements |  | Replacement resource site control requirements per OATT Part VIII, Subpart A, section 402, under the Cycle Process | A: Replacement Resource requests to have the same site control requirements as new generation interconnection requests in the Cycle Process. All site control requirements to be provided during Application Phase of Replacement Gen Process.; B: Replacement Resource requests to have the same site control requirements as new generation interconnection requests in the New Services Request Process. PJM Comment: same as Solution Option A with slightly different terminology; C: Replacement Resource requests to have the same site control requirements as new generation interconnection requests in the Cycle Process. All site control requirements to be satisfied during the Generation Replacement application Process.
18 | Application Submission Windows/Periods |  | Cycle Process - each Cycle has an Application Phase to accept Applications. See PJM Manual 14H, Section 2 "Application Phase". | A: Replacement Resource requests can be submiited to PJM at any time. There are no defined Replacement Resource request Application window/time periods.; B: IC may submit a Generation Facility Replacement application anytime prior to CIRs expiring, which is 1 year after the Actual Deactivation Date.; C: Replacement Resource requests can be submitted to PJM at any time. There are no defined Replacement Resource request Application window/time periods.
19 | Priority between Replacement Resource requests and Interconnection Requests/Cycles in the Cycle Process; Model Assumptions (More Detailed Description added in tab 2a of Matrix for additional clarity considerations) |  | Replacement Resource requests are processed in the Cycle Process with other Interconnection requests. | Replacement resource with transferred CIRs would proceed through separate generator replacement process. Two-phase study process: - Replacement Impact + Reliability Studies (RIS + RAS) - Facilities study (if needed) Target timeline of <270 days PJM Comment: this Solution Option would need to address the Design Component of how to establish Priority. This current Solution Option seems to already be included and address Design Component 11. | Replacement generator process using existing CIR's falls into the current cluster being studied and is based on the current phase of that current cluster being studied. PJM Comment: this Solution Option sounds like the Status Quo? | Use the latest completed phase 3 study of the existing or previous clusters cycle. | Use the latest completed Phase 3 models for the Cycle which has most recently completed (i.e. the Cycle has proceeded past DP3) Note: this Solution Option may be different than Solution C if Solution C only requires the Cycle to have proceeded past Phase 3, but could be during DP3. | Use the latest completed Phase 3 models for the Cycle which has most recently completed (Cycle has proceeded past Final Agreement Phase and all projects in such Cycle have GIAs fully executed) | Request will be processed under the proposed expedited Generation Facility Replacement process, rather than in the New Services Request Process. Replacement Resource study requests are processed serially in the order in which the Generation Facility Replacement application is received by PJM. PJM Comment: this Solution Option would need to address the Design Component of how to establish Priority and which model to use. | The replacement resource, along with the CIRs of the deactivating resource, will be evaluated and processed within 180 days through a stand-alone process outside of the current new interconnection services process, i.e. new generator replacement process. The replacement resource requests will be processed in the order the requests are received by PJM.
20 | Scope of Reliability studies to be performed |  | Replacement Resource requests are studied in the Cycle Process (OATT Part VIII). Main reliability studies include powerflow at various load levels, short circuit, stability, Affected System studies, TO analysis per TO Local Planning criteria. | A: Same scope of reliability studies as generation interconnection requests in the Cycle Process.; B: Because a Deactivation Resource paid for Network Upgrades at the time it originally entered service, no additional Network Upgrades will be assigned to the Replacement Resource, provided CIRs transferred are equal to or less than the Deactivation Resource and Replacement Resource is able to mitigate NUs associated with short circuit and related study results. PJM Comment: network upgrades could be assigned to the Replacement Resource due to non-CIR related issues such as energy-only MWs and different fuel types due to PJM Deliverability rules as covered in IPS PJM Training.; C: Reliability Study not required through new generator replacement process and evaluation.
21 | Cost responsibility/allocation rules for any identified required network upgrades for Replacement Resource |  | Replacement Resource requests are studied in the Cycle Process (OATT Part VIII) and network upgrades are cost allocated among all projects in a given Cycle if they meet PJM cost allocation thresholds as outlined in M14H, Att. B. | A: Interconnection facility related upgrades, if any, are 100% cost allocated to the Replacement Resource. No new reliability analysis driven network upgrades allowed. If network upgrades are identified due to the Replacement Resource, the Replacement Resource should be withdrawn from the Replacement Generation Process and can enter the PJM Cycle Process to be evalauted with other interconnection requests.; B: Interconnection facility related upgrades, if any, are 100% cost allocated to the Replacement Resource. If new reliability driven network upgrades are identified due to the Replacement Resource, the Replacement Resource will be responsible for 100% of the costs. No cost sharing/allocation between other Replacement Gen Requests or Cycle Process interconnection requests.; C: Because a Deactivation Resource paid for Network Upgrades at the time it originally entered service, no additional Network Upgrades will be assigned to the Replacement Resource, provided CIRs transferred are equal to or less than the Deactivation Resource and Replacement Resource is able to mitigate NUs associated with short circuit and related study results. PJM Comment: clarify if NUs identified, does the Replacement Resource fund 100% of the NU costs?; D: New Generation Replacement Resource requests are studied as part of the New Replacement Resource request process that occurs as a stand-alone process outside of the current new interconnection services agreement process, i.e., new generator replacement process. If network upgrades are identified due to the Replacement Resource then; 1.) The IC will be notified and provided an opportunity to sponsor the network upgrades or to modify the proposed replacement resource. 2.) If the new proposed replacement resource causes the need for network upgrades, and the IC does not seek to modify or mitigate, then the replacement resource request will be deemed withdrawn and the IC may enter the "New Service Request" process. the Replacement Resource should be withdrawn from the Replacement Generation Process and can enter the PJM Cycle Process to be evalauted with other interconnection requests.
22 | Processing of existing Replacement Generation requests at same POI (i.e. Transition Plan) |  | Replacement Resource requests are studied in the Cycle Process (OATT Part VIII) | A: Note: The CIRs already claimed by New Service Request queue positions prevent the CIRs from expiring per the PJM OATT. If these New Service Request queue positions in the Cycle Process are withdrawn and the same request allowed to enter a new Replacement Gen Process concurrently, those CIRs should remain claimed and not expire with the request moving processes. ·Requests in Expedited Process/Fast Lane (AE1-AG1) remain in Expedited Process/Fast Lane. ·Requests in Transition Cycle #1 (TC1) (AE1-AG1) remain in TC1 - TC1 is scheduled to start in Jan 2024 and be completed 3Q 2025. ·Requests in Transition Cycle #2 (TC2) (AG2-AH1) - requests would be eligible to be moved to new Replacement Gen Process. Maintain existing queue priority (between other Replacement Gen Requests) in Replacement Process as already established with their original queue submission. ·Requests in Cycle #1 (AH2 & beyond) - requests would be eligible to be moved to new Replacement Gen Process. Maintain existing queue priority (between other Replacement Gen Requests) in Replacement Process as already established with their original queue submission.; B: Request will be processed under the proposed expedited Generation Facility Replacement process, rather than in the New Services Request Process. Replacement Resource study requests are processed serially in the order in which the Generation Facility Replacement application is received by PJM. PJM Comment: how to address the existing Replacement Gen requests that already exist in the Cycle Process?; C: Replacement resources shall beprocessed separately through the new generation replacement resource process. Note: The CIRs already claimed by New Service Request queue positions prevent the CIRs from expiring per the PJM OATT. If these New Service Request queue positions in the Cycle Process are withdrawn and the same request is allowed to enter a new Replacement Gen Process concurrently, those CIRs should remain claimed and not expire with the request moving processes. ·; D: Study all the replacements in the queue at once as part of a transition. If they are clean, then they come out of the queue. If not, they stay in the clusters they are in now. Address changes to the model during the relevant retool periods.
23 | Type of interconnection service for the Replacement Generating Facility (Energy only Resource and CIRs) |  | Only Replacement resources requesting CIRs with their New Service Request application are eligible to claim and transfer CIRs from a Deactivation resource. Energy-only resources cannot claim and transfer CIRs from a Deactivation resource. | A: Interconnection Customer may request only Energy Only for the Replacement Generating Facility if the Existing Generating Facility has energy only. Interconnection Customer may request either energy and CIRs for the Replacement Generating Facility if the Existing Generating Facility has CIRs. PJM Comment: confirm if this Issue Charge (Transferring CIRs) covers an Energy-only resource deactivating and a new energy-only replacement resource to claim and transfer those energy-only rights (not CIRs). PJM OATT Part V presently only allows for CIRs to be claimed/transferred (not energy-only MWs).; B: Interconnection Customer may request only Energy Only for the Replacement Generating Facility if the Existing Generating Facility has energy only. Interconnection Customer may request either energy and CIRs for the Replacement Generating Facility if the Existing Generating Facility has CIRs. PJM Comment: confirm if this Issue Charge (Transferring CIRs) covers an Energy-only resource deactivating and a new energy-only replacement resource to claim and transfer those energy-only rights (not CIRs). PJM OATT Part V presently only allows for CIRs to be claimed/transferred (not energy-only MWs). Surplus interconnection service projects may claim CIRs equal to their capacity value following deactivation of host project. PJM Comment: If the existing resource/host project notifies PJM of Deactivation, PJM OATT Part IV section 36.4 discusses that the Surplus unit may continue Limited Operation for up to 1 year following the Actual Deactivation Date of the Generating Facility.; C: Replacement Resources that have already requested CIRs from an Existing Deactivating Resource through the existing CIR Transfer process or new generation replacement process are eligible to claim and transfer CIRs from a Deactivation resource. Interconnection Customer may request only Energy Only for the Replacement Generating Resource if the Existing Generating Resource has energy only. Interconnection Customer may request either energy and CIRs for the Replacement Generating Resource if the Existing Generating Resource has CIRs.
24 | Customer Modification of Replacement Generation Request |  | Replacement Gen requests involving CIR Transfers are studied in the PJM Cycle Process and subjected to the requirements in OATT Part VIII. Certain project changes are and are not allowed at different decision points in the Cycle Process at DP1, DP2, DP3. | A: Replacement Generating Facility can be modified any time before the evaluation process is complete.; B: After Application Phase and once Impact Study Phase starts: Cannot reduce project size (in MW) in regards to CIRs nor MFO. No fuel change allowed, no POI change allowed, no Site changes allowed. Equipment changes (Permissible Technological Advancement changes only) can occur and be captured via Necessary Study after GIA.; C: Replacement Generating Facility can be modified any time before the evaluation process is complete. PJM Comment: this is Solution Option A; D: Replacement Resource requests can be modified at any time before the evaluation process is complete.
25 | Clear definition of "material adverse impact(s)." |  | No present PJM Tariff definition for "material adverse impacts" exists. Note: "Material Modification" is a PJM Tariff defined term and is included as Design Component #4 above. | A: "Material adverse impact": If the Replacement Resource degrades any thermal, short circuit, stability capability available on the system, as compared to the Deactivation Resource. In other words, does the Replacement Resource consume available transmsision capability (i.e. headroom) from the system in excess of what the Deactivation Resource already utilized. This can be done without triggering a reliability criteria violation and the requirement for a network upgrade.; B: "Material adverse impact" only if the Replacement Resource causes a reliability criteria violation and the requirement for a network upgrade. Replacement Resource allowed to consume available transmission capability (i.e. headroom) from the system in excess of what the Deactivation Resource already utilized, as long as no reliability criteria violations are identified.; C: "Material adverse impact" only if the Replacement Resource causes a reliability criteria violation and the requirement for a network upgrade. Replacement Resource allowed to consume available transmission capability (i.e. headroom) from the system in excess of what the Deactivation Resource already utilized, as long as no reliability criteria violations are identified. PJM Comment: this is Solution Option B; D: Material Adverse Impact: Defined as any CIR Transfer requests in the new generation replacement process from a replacement resource request for resources interconnecting at the same CIR level or below and at the same POI is evaluated and processed to determine if the proposed transfer of CIRs or replacement resource will result in a substantial materially adverse impact to the transmission system, i.e., impacts stability and short-circulate limits, including power flow during normal or contingency conditions, results in any substantial increase in the short circuit duty impacts, or adverse angular or voltage stability impacts, as compared to the impacts associated with the original Generating Unit. Requests deemed to have an adverse material impact would be required to be processed through the PJM New Service Request Interconnection Request process. In other words, does the Replacement Resource consumes available transmission capability (i.e., headroom) from the system in excess of what the Deactivation Resource already utilized.; E: New network upgrades are considered Material Adverse Impacts
26 | Priority between Replacement Resource requests and Interconnection Requests/Cycles in the Transmission Owner and PJM Engineering Resource Allocation |  | Existing PJM parallel processes include interconnection studies, interim deliverability studies, upgrade request studies, affected system studies, surplus service request studies. Need to consider these other parallel studies outside the cycle in the solution. | A: Request will be processed under the proposed expedited Generation Facility Replacement process, rather than in the New Services Request Process. Replacement Resource study requests are processed serially in the order in which the Generation Facility Replacement application is received by PJM.; B: Depends on whether the new resource will replace an RMR; C: The CIRs already claimed by New Service Request queue positions prevent the CIRs from expiring per the PJM OATT. If these New Service Request queue positions in the Cycle Process are withdrawn in order for the same request to enter a new Replacement Generation Process concurrently, those CIRs should remain claimed and not expire with the request moving through any of PJM's processes:(1) Expedited Process/Fast Lane (AE1-AG1); (2) Transition Cycle #1 (TC1) (AE1-AG1); (3) Post 2026 New Services Submissions. Existing CIR Transfer Requests from deactivating or anticpated deactivating resources would be eligible to be moved to the new Replacement Generation Process upon election by the replacement resource and will be processed in the order the requests are received by PJM.; D: PJM should utilize pre-approved outside consultants to minimize impact to engineering resources.
27 | CIR Holder (Ownership) |  | The transfer of the CIR has to be between the present holder as the deactivating resource and the replacement resource. If different, there is a notice of CIR transfer form to capture the transfer and/or selling of the CIR's to the new holder. | A: The CIRs are not transferred bilaterally. The CIRs are made available to the next resource(s) in the queue.; B: The transfer of the CIR has to be from the present CIR holder as the deactivating or anticipated deactivating resource to the replacement resource holder or newly identified CIR transfer recipient. If the present CIR holder or deactivating or anticipated deactivating resource and replacement resource holder/CIR Transfer recipient are different, a notice of CIR transfer form shall be submitted to capture the transfer and/or selling of the CIRs to the new holder.
28 | Contingent Facilities |  | Contingent Facilities (unbuilt Interconnection Facilities and/or Network Upgrades) which the New Service Request is dependent upon are identified in the Cycle Process Phase I, II, and III System Impact Studies and are documented in the GIA. Examples of these can include planned baseline upgrades or required Network Upgrades being funded by previosuly queued interconnection projects. | A: Contingent Facilities, if any, would be identified during the Replacement Resource Impact Study and captured in the GIA.
29 | Interim Studies |  | Required for Cycle Process Interconnection requests if 1) coming into service prior to their case study year or 2) coming into service prior to the completion of any required network upgrade or contingent facility that the interconnection request requires or is dependent upon to support their interconnection request. | A: Same Interim study rules as Status Quo would apply to Replacement Resources outside the Cycle Process
Instructions:
*Implementation should consider timing for both PJM and stakeholders (added as standard component based on Stakeholder feedback- 2015)
1Design Components - each is an "attibute" or "component" of any proposed solution. Consensus of the group should be sought on selection of a set of solution criteria.
2Solution Options - each is a solution alternative elicited from the stakeholder group that meet one of the specific solution criteria.
To complete the matrix:
1. Elicit from the stakeholder group a set of components (attributes) desired for any proposed solution. Enter a short label for each in the Design Components column.
2. If needed, enter a more detailed description of each criteria on the "Design Component Details" tab (2a).
3. Using informal feedback from the participants, rate each component's priority in the final solution as "high/medium/low"
4. Elicit from the stakeholder group potential solution alternative(s) for each component. Enter a short label for each in the Solution Options columns.
5. If needed, enter a more detailed description of each potential solution option on the "Option Details" tab 2b.
6. Once the matrix is filled out, the group will attempt to select a single solution alternative (column) for each component (row) to form a solution "package", to be documented in tab 3, "Packages Matrix".
Example: cells 1B, 2C, 3A, 4B, 5D could make up a solution package.

## 2a. Design Component Details
Interconnection Process Subcommittee
Capacity Interconnection Rights (CIR) Transfer Efficiency
COMPONENT DETAILS
Instructions: Complete this form as needed. Design components should be populated from the Options Matrix.
Design Component |  | Detailed Description
19 | Priority between Replacement Resource requests and Interconnection Requests/Cycles in the Cycle Process | Priority between these 2 types of requests needs to be clearly established in order to determine basecase models to be used for each study, which forms the basis for how available system capability is allotted. Example 1: For a Replacement Resource study, which Interconnection Requests or which Cycle of projects in the Cycle Process should be included in the model used to study the Replacement Resource. Example 2: For a Cycle study, which Replacement Resource requests should be included in the model used to study the Cycle.
11 | Screening criteria, Study Phases, and scope of each Study Phase | Screen scenarios: 1. Base: Standard interconnection Queue base case with existing generator (potential for relatively small adjustments, e.g. tuning); 2. Study: same as base case, but existing generator is removed and new generator added in its place Reductions in short circuit current: No adverse impact is expected for reductions in short circuit current Study summer peak and shoulder cases for all fuel types and use fuel type based dispatching, and additional study of charging scenario for battery
11 | Screening criteria, Study Phases, and scope of each Study Phase | Screen scenarios: 1. Base: Standard interconnection Queue base case with existing generator (potential for relatively small adjustments, e.g. tuning); 2. Study: same as base case, but existing generator is removed and new generator added in its place Reductions in short circuit current: Study reports on the short-circuit values, TO identifies if upgrades are needed. Stability analysis is performed on all available stability seasons, with respect to the base standard interconnection queue model set. Short-circuit is performed on the suStability analysis is performed on all available stability seasons, with respect to the base DISIS model set. Short-circuit is performed on the summer stability models.
4 |  | <enter detailed description of this component>
5 |  | <enter detailed description of this component>

## 2b. Option Details
Interconnection Process Subcommittee
Capacity Interconnection Rights (CIR) Transfer Efficiency
SOLUTION OPTION DETAILS
Instructions: Complete this form as needed, including more detailed / expansive descriptions of options than the Options Matrix allows.
Cell # | Detailed Description
Corresponding cell number from Options Matrix (ex. 1A, 1B, 2A, etc.) | <enter detailed description of this option>

## 3. Package Matrix
Interconnection Process Subcommittee
Capacity Interconnection Rights (CIR) Transfer Efficiency
PACKAGE/ PROPOSAL MATRIX
Packages
# | Design Components | Priority | Status Quo | A | B | C | D | E
1 | Eligible deactivating resources |  | All resources provided that the resource has CIRs (i.e. Generation Capacity Resources) & the resource has submitted an official deactivation notice to PJM
2 | Eligible replacement resources |  | All resources including storage devices provided that the resource has requested CIRs with their New Serivce Request application (i.e. requested to be a Generation Capacity Resource)
3 | Criteria for determining a transfer under this process is permissible |  | All generation resources provided that the resources have CIRs (i.e. Generation Capacity Resource). The same CIR holder for both the deactivation resource and the replacement resource. A deactivation notice submitted to PJM. Submission of a new service request application and notice to intent to transfer CIRs form prior to CIRs expiring.
4 | New/Modified Definitions (i.e. Material Modification) |  | Material Modification OATT Part VIII, Subpart A, section 400 Definitions “Material Modification” shall mean, as determined through a Necessary Study, any modification to a Generation Interconnection Agreement that has a material adverse effect on the cost or timing of Interconnection Studies related to, or any Distribution Upgrades, Network Upgrades, Stand Alone Network Upgrades or Transmission Owner Interconnection Facilities needed to accommodate, any Interconnection Request with a later Cycle.
5 | Public Posting of Replacement Generation Requests |  | CIR transfers to replacement resources are assigned a PJM project identifier within the PJM New Service Request process and posted to the PJM New Service Request webpage
6 | POI Requirements of Replacement Resource |  | Replacement generation resource is not required to be located at the same Point of Interconnection (POI) as the Deactivation generation resource
7 | MW Requirements of Replacement Resource |  | The holder of the CIRs will retain only such rights that are commensurate with the size in megawatts of the replacement generation, not to exceed the amount of the holder’s Capacity Interconnection Rights associated with the facility upon Deactivation or removal of Capacity Resource status. The replacement gen request has no upper limit on the CIRs, nor the MFO they are requesting with their generation interconnection New Service Request.
8 | Initiation of CIR Transfer Process |  | The same CIR holder for deactivation resource and replacement resource. Requirement of a deactivation notice to PJM. Once a deactivation notice has been received by PJM, Submission of new service request application and notice of intent to transfer CIRs form prior to CIRs expiring, which is 1 year after the Actual Deactivation Date.
9 | Commercial Operation date of replacement generation |  | As determined in the GIA.
10 | Priority among Replacement Resource requests |  | The Replacement generation resource, along with the CIR Transfer, is evaluated and processed as part of the PJM New Services Request Process.
11 | Screening criteria, Study Phases, and scope of each Study Phase (More Detailed Description added in tab 2a of Matrix for additional clarity considerations) The screening criteria includes an assessment of whether the replacement resource would trigger network upgrades |  | Transfers of CIRs are evaluated through System Impact Studies (Phases 1-3 of Cycle Process) performed by PJM (including load flow, short circuit and stability).
12 | Criteria for Generator Replacement Requests that are found to have adverse impacts to transmission system |  | The Replacement generation resource is part of a Cycle within the PJM New Services Request Process and cost responsibility may be shared with other New Service Requests in the same Cycle, if impacts are found
13 | Application and Deposit Requirements for Replacement Resource |  | Applicant must submit any claim from the deactivating generating units with their application, and it must be received by the Application Deadline. CIR claims must be submitted using the CIR Transfer template available on the PJM website. Deposit based on PJM's new process.
14 | Decision Points during Study Process |  | There are decision points 1, 2, and 3 after Phases 1,2,3 of the Cycle Process.
15 | GIA Requirements |  | GIA issued for Replacement resource as part of the New Services Request Process, per the OATT sections covering the New Services Request Process
16 | Cost responsibility/allocation rules for any identified required network upgrades for Replacement Resource |  | Replacement Resource requests are studied in the Cycle Process (OATT Part VIII) and network upgrades are cost allocated among all projects in a given Cycle if they meet PJM cost allocation thresholds as outlined in M14H, Att. B.
17 | Processing of existing Replacement Generation requests at same POI (i.e. Transition Plan) |  | Replacement Resource requests are studied in the Cycle Process (OATT Part VIII)
18
19
20
21
22
23
24
25
26
27
28
29 | [8 empty] | Low
30 | [8 empty] | Low - Medium
Low - High
Medium
Instructions: | [8 empty] | Medium - High
1. Copy over design component, priority, and status quo columns from options matrix | [8 empty] | High
2. Complete individual packages in columns by selecting individual component options from the options matrix.

## 3a. Package Details
Interconnection Process Subcommittee
Capacity Interconnection Rights (CIR) Transfer Efficiency
PACKAGE / PROPOSAL DETAILS
Instructions: Complete this form as needed, including more detailed / expansive descriptions of package components than the Package Matrix allows.
Package Solutions2
| A | B | C | D | E
1 | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component>
2 | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component>
3 | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component>
4 | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component>
5 | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component>

## Parking Lot
Interconnection Process Subcommittee
Capacity Interconnection Rights (CIR) Transfer Efficiency
PARKING LOT
Instructions: Use this space to document any items not specific to another topic area.
Description

## Revision History
Interconnection Process Subcommittee
Capacity Interconnection Rights (CIR) Transfer Efficiency
Revision History
Current Spreadsheet Version:
Instructions: Document all version changes to this matrix for easy identification of changes.
Version | Posting Date | Description of changes
1
2
3