## Version History
PJM 2015 RTEP Proposal Window #1 Tracking Spreadsheet
Proposal Window: | 2015 RTEP Proposal Window 1
Window Opening Date: | 2015-06-18
Window Closing Date: | 2015-07-20
Current Spreadsheet Version | V1
V1: Original Posting for 8/13/2015 TEAC

## Tracking By Proposal
PJM 2015 RTEP Proposal Window #1 Tracking Spreadsheet
Proposal Window: | 2015 RTEP Proposal Window 1
Window Opening Date: | 2015-06-18
Window Closing Date: | 2015-07-20
Current Spreadsheet Version | V1
Project ID | Upgrade/Greenfield | Proposing Entity | Final Project Cost ($M) | Target Zone(s) | kV Level(s) | Analysis Type | FG# | Major Components/Project Description
2015_1-1A | Upgrade | Dominion | 17.54 | Dominion | 230 | Gen Deliv | NEW-32, NEW-34, NEW-36, NEW-37 | Rebuild 11.03 miles of existing line between Chesterfield and Charles City.
2015_1-1B | Upgrade | Dominion | 73 | Dominion | 500 | Gen Deliv | NEW-52 | Rebuild 500kV line from Rogers Rd - Carson with new structures
2015_1-1C | Greenfield | Dominion | 106.3 | Dominion | 500 | Gen Deliv | NEW-52 | New 32 miles long 500kV line from Carson - Rogers Rd
2015_1-1D | Greenfield | Dominion | 78.9 | Dominion | 500 | Gen Deliv | NEW-52 | 23 miles of new 500kV line from Carson - Rawlings
2015_1-1E | Greenfield | Dominion | 53.4 | Dominion | 500/230 | Gen Deliv | NEW-52 | A short 500kV line from Rogers Rd substation to new substation called Maclins. A 500/230kV TX at Maclins and a 4 mile 230kV line from Maclins to Clubhouse.
2015_1-1F | Greenfield | Dominion | 67 | Dominion | 230 | Gen Deliv | NEW-52 | A 500/230kV TX at Rawlings and a new 230kV line from Rawlings to new 230kV station at Purdy. Purdy cuts into the existing Carson - Clubhouse 230kV (238 line) line approximately 8.7 miles from Clubhouse.
2015_1-2A | Upgrade | AEP | 5.36 | AEP | 138 | N-1-1 Thermal; N-1-1 Voltage Drop | N2-T4, N2-T5, N2-T6, N2-T7, N2-T8, N2-T9, N2-T10, N2-T11, N2-T12, N2-T13, N2-T14, N2-T15; N2-VM65, N2-VM66, N2-VM67, N2-VM68, N2-VM69; N2-VD75, N2-VD76, N2-VD77, N2-VD78, N2-VD79, N2-VD80, N2-VD81, N2-VD82, N2-VD83, N2-VD84, N2-VD85, N2-VD86, N2-VD87, N2-VD88, N2-VD89, N2-VD90 | Tams Mountain Area Uprates
2015_1-2B | Upgrade | AEP | 1.25 | AEP | 138 | Gen Deliv | 801 | Lebanon, Elk Garden Switch Replacements
2015_1-2C | Upgrade | AEP | 2.5 | AEP | 138 | Gen Deliv | 83,85,87,88,89,657,658,659,660,827,188,189,190,194,196,117,119,120,121,125,648,649,817,93,95,96,97,99,640,641,801,166,884 | Clinch River Area Ratings Uprates
2015_1-2D | Greenfield | AEP | 38.5 | AEP | 138 | Gen Deliv | 83,85,87,88,89,657,658,659,660,827,188,189,190,194,196,117,119,120,121,125,648,649,817,93,95,96,97,99,640,641,801,166,884 | Construct 22 miles of new 1033 ACSR line between Clinch River and Keen Mtn 138kV stations
2015_1-2E | Greenfield | AEP | 95 | AEP | 138 | Gen Deliv | 83,85,87,88,89,657,658,659,660,827,188,189,190,194,196,117,119,120,121,125,648,649,817,93,95,96,97,99,640,641,801,166,884 | Construct 43 miles of new 1033 ACSR line between Clinch River and Beaver Creek 138kV stations
2015_1-2F | Upgrade | AEP | 0.144 | AEP | 138 | N-1; Gen Deliv | 152;865 | Replace the Muskingum 138 kV bus #1 and bus #2
2015_1-2G | Greenfield | AEP | 25.6 | AEP | 345 | Gen Deliv | 59 | Construct Dequine-Meadow Lake 345 kV ckt #3. Install a 3000 A (cont. current) 63 kA (intr. current) 345 kV circuit breaker at Dequine station to complete breaker and half string “A”. Swing Fowler Ridge (IPP), Meadow Lake #1, and Meadow Lake #2 to new positions. Terminate Meadow Lake #3 between breaker C1 and C. Install a 3000 A (cont. current) 63 kA (intr. current) 345 kV circuit breaker at Meadow Lake station to complete breaker and half string “D”. Swing Dequine #1 and #2 to new positions. Terminate Dequine #3 between breaker C and C1. Dequine-Meadow Lake ckt #1 and ckt #2 will continue to be on carrier communications whereas; ckt #3 will be on fiber communications.
2015_1-2H | Upgrade | AEP | 10.6 | AEP | 345/138 | Gen Deliv | 653 | Install a second 345/138kV, 675 MVA Transformer at Desoto. The new transformer will be connected to the 345kV bus via a new motorized switch while two breakers will be used to connect it to the 138kV.
2015_1-2I | Upgrade | AEP | 27.5 | AEP | 345 | Gen Deliv | 59 | Rebuild Dequine-Meadow Lake 345 kV ckt 1 and ckt 2 using two (2) bundled 954 ACSR 54/7 Cardinal conductor.
2015_1-2J | Upgrade | AEP | 26.6 | AEP | 345 | Gen Deliv | 59 | Rebuild dequine-Meadow Lake 345 kV ckt 1 and ckt 2 using three (3) bundled 954 ACSR 54/7 Cardinal conductor.
2015_1-2K | Upgrade | AEP | 5.1 | AEP | 345 | Gen Deliv | 59 | Reconductor Dequine-Meadow Lake 345 kV ckt 1 utilizing dual 954 ACSR 54/7 Cardinal conductor.
2015_1-2L | Greenfield | AEP | 25.82 | AEP | 138 | N-1-1 Thermal; N-1-1 Voltage Magnitude; N-1-1 Voltage Drop | N2-T16, N2-T17; N2-VM70, N2-VM71, N2-VM72, N2-VM73, N2-VM74, N2-VM75, N2-VM76; N2-VD73, N2-VD74 | Construct Herlan station as breaker and a half configuration with 9-138kV CB's on 4 strings and with 2-28.8 MVAr capacitor banks.
2015_1-3A | Upgrade | AEP/DEOK | 5.95 | AEP/DEOK | 345 | Gen Deliv | NEW-4, NEW-7, NEW-8, NEW-9, NEW-33 | This is a joint proposal between AEP and Duke Energy, Ohio & Kentucky. Perform a sag study to include LiDAR survey on AEP portion (0.36 miles) of the Tanners Creek to Miami Fort 345kV Circuit. A successful sag study will allow AEP's conductor to be operated at its Maximum Operating Temperature and thus increase the Summer Emergency rating from 1409 MVA to 1956 MVA on AEP's side of the tie line. If the sag study determines the tie line cannot be operated at its MOT without additional improvements, in the worst case scenario, AEP would need to reconductor their portion of the line; which is expected to cost approximately $400K. Replace the DEO&K portion (3.4 miles) of the Tanners Creek to Miami Fort 345kV circuit with two different types of conductor. Aluminum Conductor Composite Reinforced will be used for the Ohio River crossing with the balance of the circuit using Aluminum Conductor, Steel Supported. The rating for the Duke portion of the circuit will increase to 2151MVA.
2015_1-4A | Upgrade | First Energy | 5.1 | ATSI | 138 | Gen Deliv | 664 | Rebuild the existing double-circuit tower line section from Beaver Substation to Brownhelm Jct, approx. 2.8 miles, to reconductor with new 954 kcmil ACSS.
2015_1-4B | Upgrade | First Energy | 1.015 | ATSI | 138 | N1-VM; N-1 Voltage Drop | N1-VM2,N1-VM3,N1-VM4,N1-VM5,N1-VM6,N1-VM7,N1-VM8,N1-VM9,N1-VM10,N1-VM11,N1-VM12,N1-VM13; N1-VD2, N1-VD3 | Add a 138kV 36 MVar Capacitor Bank and associated capacitor switcher at Lincoln Park Substation. Extend the 138kV Bus in order to accommodate the Capacitor Bank.
2015_1-4C | Upgrade | First Energy | 4.6 | ATSI | 138 | N-1-1 Thermal | N2-T1, N2-T2, N2-T3 | Rebuild the 6.6 mi 477 ACSR Evergreen to Ivanhoe 138 kV line to 477 ACSS.
2015_1-4D | Modeling Correction | First Energy | N/A | ATSI | 69 | N-1 Voltage Drop | N1-VD8,N1-VD9,N1-VD10,N1-VD11,N1-VD12,N1-VD13,N1-VD14,N1-VD15,N1-VD16,N1-VD17,N1-VD18,N1-VD19,N1-VD20,N1-VD21,N1-VD22,N1-VD23,N1-VD24,N1-VD25,N1-VD26,N1-VD27,N1-VD28,N1-VD29,N1-VD30,N1-VD31,N1-VD32,N1-VD33,N1-VD34,N1-VD35,N1-VD36,N1-VD37,N1-VD38,N1-VD39,N1-VD40,N1-VD41,N1-VD42,N1-VD43,N1-VD44,N1-VD45 | Modeling Corrections: A combination of transformer modeling corrections at Midway Substation due to impending transformer replacements, and energizing the capacitor bank at Pemberville Substation pre-contingency eliminates these violations
2015_1-4E | Upgrade | First Energy | 5.924 | JCPL | 230 | N-1-1 Voltage Drop | N2-VD68 | Install 1-230 kV breaker at East Windsor and construct new 230 kV line terminal. Install 2-230 kV breakers at Windsor and construct new 230 kV line terminal. Convert the F2006, 230 kV line, East Windsor-Windsor 230 kV from six-wire construction to two 230 kV three-wire circuits. The rating of the new circuit will be: SN: 709 MVA, SE: 869 MVA, WN: 805 MVA, and WE: 1031 MVA
2015_1-4F | Upgrade | First Energy | 1.5 | JCPL | 230 | N-1 Voltage Drop; N-1 Voltage Magnitude; N-1-1 Voltage Magnitude; N-1-1 Voltage Drop | N1-VD1; N1-VM1; N2-VM5, N2-VM6, N2-VM7, N2-VM8, N2-VM10, N2-VM12, N2-VM13; N2-VD2, N2-VD3, N2-VD4 | Install 1-230 kV breaker and a 72 Mvar fast-switched capacitor at Englishtown
2015_1-4G | Upgrade | First Energy | 0.013 | APS | 138 | Gen Deliv | 589, 859, 860, 861 | Change the CT Ratio at Seneca Caverns from 120/1 to 160/1 and adjust relay settings accordingly. The rating of all equipment not explicitly listed shall exceed: SN: 152 MVA, SE: 152 MVA, WN: 152 MVA, and WE: 152 MVA
2015_1-4H | Upgrade | First Energy | 2.5 | Penelec | 115 | N-1-1 Voltage Drop | N2-VD46,N2-VD47,N2-VD53,N2-VD60,N2-VD61,N2-VD72 | Install two 23.8 MVAR 120.8kV nameplate (21.6 MVAR 115kV effective) capacitors at Shade Gap.
2015_1-4I | Upgrade | First Energy | 0.725 | Penelec | 115 | N-1-1 Voltage Magnitude; N-1-1 Voltage Drop | N2-VM26,N2-VM27,N2-VM28,N2-VM29,N2-VM30,N2-VM31,N2-VM32,N2-VM33,N2-VM34,N2-VM35,N2-VM36,N2-VM37,N2-VM38,N2-VM39,N2-VM40,N2-VM48,N2-VM49,N2-VM50,N2-VM51,N2-VM52,N2-VM53,N2-VM54,N2-VM55,N2-VM56,N2-VM57,N2-VM58,N2-VM59,N2-VM60,N2-VM61,N2-VM62,N2-VM63,N2-VM64,N2-VM77,N2-VM78,N2-VM79,N2-VM80,N2-VM81,N2-VM82,N2-VM9; N2-VD10,N2-VD11,N2-VD12,N2-VD13,N2-VD14,N2-VD15,N2-VD16,N2-VD17,N2-VD18,N2-VD19,N2-VD20,N2-VD21,N2-VD22,N2-VD23,N2-VD24,N2-VD25,N2-VD26,N2-VD27,N2-VD28,N2-VD29,N2-VD30,N2-VD31,N2-VD32,N2-VD33,N2-VD34,N2-VD35,N2-VD36,N2-VD37,N2-VD38,N2-VD39,N2-VD54,N2-VD55,N2-VD56,N2-VD57,N2-VD58,N2-VD59,N2-VD62,N2-VD63,N2-VD64,N2-VD65,N2-VD69,N2-VD70,N2-VD71,N2-VD91,N2-VD92 | Install a 115kV breaker on the Hooversville #1 Transformer
2015_1-4J | Upgrade | First Energy | 0.383 | Penelec | 115 | N-1-1 Voltage Magnitude; N-1-1 Voltage Drop | N2-VM11,N2-VM14,N2-VM15,N2-VM16,N2-VM17,N2-VM18,N2-VM19,N2-VM20,N2-VM21,N2-VM22,N2-VM23,N2-VM24,N2-VM25; N2-VD41,N2-VD42,N2-VD43,N2-VD44,N2-VD45,N2-VD48,N2-VD49,N2-VD50,N2-VD51,N2-VD52 | Install a 115kV breaker on the Eclipse #2 115/34.5kV transformer.
2015_1-4K | Upgrade | First Energy | 1.5 | Penelec | 115 | N-1-1 Voltage Magnitude; N-1-1 Voltage Drop | N2-VM1, N2-VM2, N2-VM3, N2-VM4; N2-VD40 | Install a 39.7 MVAR 120.8kV capacitor (115kV 36.0MVAR effective) at Central City West substation, one capacitor switcher, and capacitor protection relays.
2015_1-4L | Upgrade | First Energy | 1.518 | Penelec | 115 | N-1-1 Voltage Drop | N2-VD5,N2-VD6,N2-VD7,N2-VD8,N2-VD9 | Install a 39.7 MVAR 120.8kV (36 MVAR 115kV effective) capacitor bank and assoicated facilities at Morgan Street Substation
2015_1-4M | Upgrade | First Energy | 2.066 | Penelec | 115 | N-1 Voltage Drop | N1-VD7 | Install 115kV Venango Jct. line breaker at Edinboro South.
2015_1-4N | Upgrade | First Energy | 1.419 | Penelec | 115 | N-1 Voltage Drop | N1-VD5, N1-VD6 | Install a second 115kV 3000A 40kA bus tie breaker at Hooversville substation
2015_1-4O | Upgrade | First Energy | 13.25 | Penelec | 115 | N-1 Voltage Drop | N1-VD4 | Convert East Towanda to a 115kV breaker and a half layout and upgrade remote terminal relaying.
2015_1-4P | Upgrade | First Energy | 0.6 | Penelec | 115 | N-1 Thermal; Gen Deliv | 204, 674 | Replace wave trap, bus conductor and relay at Hilltop substation. Replace remote end relays at Prospect and Cooper substations. New rating of line will be SN: 249 MVA SE: 300 MVA
2015_1-5A | Greenfield | Transource | 15.3 | AEP/DEOK | 345 | Gen Deliv | NEW-4, NEW-7, NEW-8, NEW-9, NEW-33 | Construct new greenfield 345kV Switch Station to be called Anson Station. The existing Tanners Creek-East Bend 345kV, East Bend-Terminal 345kV and Miami Fort-Terminal 345kV circuits will all be looped in and out of this station. The station will consist of six new 345kV breakers and will be configured in a ring bus.
2015_1-5B | Greenfield | Transource | 11.4 | APS/Penelec | 115 | N-1-1 Voltage Drop | N2-VD41,N2-VD42,N2-VD43,N2-VD44,N2-VD45,N2-VD48,N2-VD49,N2-VD50,N2-VD51,N2-VD52 | Establish a new 115kV circuit from Burma station (APS) to Piney station (PENELEC). This plan will require the installation of a second 138/115kV transformer at Burma, installed on the #2 138kV bus, to serve the new line. This new circuit will eliminate the voltage drop violations caused by N-1-1 contingency combinations which involve the loss of the existing Burma - Piney 115kV circuit as well as the existing Burma 138/115kV transformer.
2015_1-5C | Greenfield | Transource | 21.4 | Penelec/Meted | 500/115 | N-1, Gen Deliv, N-1-1 Voltage Magnitude, N-1-1 Voltage Drop | 204; 674; N2-VM1,N2-VM2,N2-VM3,N2-VM4, N2-VM9,N2-VM26,N2-VM27,N2-VM28,N2-VM29,N2-VM30,N2-VM31,N2-VM32,N2-VM33,N2-VM34,N2-VM35,N2-VM36,N2-VM37,N2-VM38,N2-VM39,N2-VM40,N2-VM48,N2-VM49,N2-VM50,N2-VM51,N2-VM52,N2-VM53,N2-VM54,N2-VM55,N2-VM56,N2-VM57,N2-VM58,N2-VM59,N2-VM60,N2-VM61,N2-VM62,N2-VM63,N2-VM64,N2-VM77,N2-VM78,N2-VM79,N2-VM80,N2-VM81,N2-VM82; N2-VD10,N2-VD11,N2-VD12,N2-VD13,N2-VD14,N2-VD15,N2-VD16,N2-VD17,N2-VD18,N2-VD20,N2-VD21,N2-VD22,N2-VD23,N2-VD24,N2-VD25,N2-VD26,N2-VD27,N2-VD28,N2-VD29,N2-VD30,N2-VD31,N2-VD32,N2-VD33,N2-VD34,N2-VD35,N2-VD36,N2-VD37,N2-VD38,N2-VD40,N2-VD54,N2-VD55,N2-VD56,N2-VD57,N2-VD58,N2-VD59,N2-VD62,N2-VD63,N2-VD64,N2-VD65,N2-VD69,N2-VD70,N2-VD71,N2-VD91,N2-VD92 | Construct a new 500/115kV Station referred to as Cambria Station by tapping the existing Conemaugh-Hunterstown 500kV Line. The proposed station will cut into the existing Claysburg-Salix (via Krayn) 115kV line. Additionally, install a 24.4 Capacitor Bank at Hooversville station with SCADA control. Additional SCADA upgrades at Saxton and Somerset.
2015_1-5D | Greenfield | Transource | 22.9 | APS/Penelec | 138;115 | N-1-1 Voltage Drop | N2-VD46,N2-VD47,N2-VD53,N2-VD60,N2-VD61,N2-VD72 | Construct new greenfield 138kV line (approximately 11.7 miles) between Carlisle Pike and Fayetteville substations. Install 138/115kV transformer at Carlisle Pike to accommodate new 138kV line. Install 4 138kV breakers at Fayetteville for reliability and contingency purposes. Install four 115kV breakers and a high side 138kV breaker for the proposed transformer at Carlisle Pike for reliability and contingency purposes.
2015_1-5E | Greenfield | Transource | 16.818 | APS/Penelec | 115 | N-1-1 Voltage Drop | N2-VD46,N2-VD47,N2-VD53,N2-VD60,N2-VD61,N2-VD72 | Install a new 230/115kV Transformer at Rice Station (proposed as part of the PJM 2014 LTW, Proposal 1-9A) and construct a new greenfield 115kV line from Rice to Carlisle Pike. Install additional 115kV breakers at Carlisle Pike to reduce exposure and increase reliability.
2015_1-5F | Greenfield | Transource | 65.3 | Dominion | 500 | Gen Deliv | NEW-52 | Establish a new 500kV circuit from Carson station to Rawlings station. This new circuit will eliminate the violation for the generation deliverability flowgate involving Carson - Rodgers Road 500kV Circuit for the loss of the existing Carson - Rawlings 500kV Circuit.
2015_1-5G | Greenfield | Transource | 19.3 | AEP/DEOK | 345 | Gen Deliv | NEW-4, NEW-7, NEW-8, NEW-9, NEW-33 | Construct new greenfield 345kV line between Tanners Creek and Miami Fort substations effectively creating Tanners Creek-Miami Fort 345kV Circuit #2. Install two 345kV breakers at Tanners Creek to accommodate proposed line. Install one 345kV breaker at Miami Fort to accommodate new line.
2015_1-6A | Greenfield | Nextera | 105 | Dominion | 500/230 | Gen Deliv | 52 | New Pleasant Shade 500/230 kV substation, New 4.2 mile 500 kV transmission line connecting Pleasant Shade to Rogers Road, and New 22-mile 500 kV transmission line connecting Carson to Rawlings.
2015_1-6B | Greenfield | Nextera | 51 | Dominion | 500 | Gen Deliv | 52 | New 22 mile transmission line from Carson - Rawlings 500 kV
2015_1-6C | Greenfield | Nextera | 61.8 | Dominion | 500 | Gen Deliv | 52 | New 28 mile transmission line from Rogers Road - Carson 500 kV
2015_1-7A | Greenfield | PSEG | 34.2 | AEP | 345 | Gen Deliv | 59 | New 345kV line from Dequine to Meadow Lake
2015_1-7B | Greenfield | PSEG | 39.8 | JCPL | 230 | N-1 Voltage Drop; N-1 Voltage Magnitude; N-1-1 Voltage Magnitude; N-1-1 Voltage Drop | N1-VD1; N1-VM1; N2-VM5, N2-VM6, N2-VM7, N2-VM8, N2-VM10, N2-VM12, N2-VM13; N2-VD2, N2-VD3, N2-VD4 | Build a new 230kV line from East Windsor to Englishtown
2015_1-7C | Greenfield | PSEG | 48.5 | JCPL | 500/230 | N-1 Voltage Drop; N-1 Voltage Magnitude; N-1-1 Voltage Magnitude; N-1-1 Voltage Drop | N1-VD1; N1-VM1; N2-VM5, N2-VM6, N2-VM7, N2-VM8, N2-VM10, N2-VM12, N2-VM13; N2-VD2, N2-VD3, N2-VD4 | Build a new 500-230kV Station on the existing Deans - Smithburg line at Englishtown
2015_1-7D | Greenfield | PSEG | 47.5 | Dominion | 500/230 | Gen Deliv | NEW-52 | Build a three (3) breaker 500kV ring bus on Brunswick to Wake 500kV line. Add one (1) transformer and 230kV circuit from ring bus to Clubhouse 230kV station.
2015_1-7E | Greenfield | PSEG | 16.5 | ATSI | 138 | Gen Deliv | 664 | New 138kV line from Beaver to Black River
2015_1-7F | Greenfield | PSEG | 19.1 | ATSI | 138 | Gen Deliv | 664 | New 138kV line from Beaver to Lake Ave.
2015_1-7G | Greenfield | PSEG | 39 | ATSI | 138/69 | Gen Deliv | 664 | Build new 138kV Sheffield station that taps Beaver to Johnson 138kV line. Build a new overhead 138kV line from Black River to new Sheffield station. Install a new 138kV breaker at Black River. Construct new 138/69kV station that taps the Baumhart to Elyria 69kV line. Construct new 138kV line from Beaver to new 138/69kV station. Install a new 138kV breaker at Beaver station.
2015_1-7H | Greenfield | PSEG | 135.8 | AEP | 138 | N-1-1 Thermal | N2-T10, N2-T11, N2-T12, N2-T14, N2-T4, N2-T5, N2-T6, N2-T8 | New 138kV line from Guyandotte to Tams Mountain
2015_1-7I | Greenfield | PSEG | 61.6 | AEP | 345/138 | N-1-1 Thermal; N-1-1 Voltage Magnitude; N-1-1 Voltage Drop | N2-T10,N2-T11,N2-T12,N2-T13,N2-T14,N2-T15; N2-VM65,N2-VM66,N2-VM67,N2-VM68,N2-VM69; N2-VD75,N2-VD76,N2-VD77,N2-VD78,N2-VD79,N2-VD80,N2-VD81,N2-VD82 | Tap the existing Kanawha River – Matt Funk 345kV line to Bradley – Poleyard 138kV line at a new substation with a 345/138kV transformer
2015_1-7J | Greenfield | PSEG | 18.5 | ATSI | 138 | N-1 Voltage Magnitude | N1-VM2, N1-VM4, N1-VM6, N1-VM8, N1-VM10, N1-VM11, N1-VM12 | Build new 138kV line betweeen Crossland and Elwood
2015_1-7K | Greenfield | PSEG | 17.9 | ATSI | 138 | N-1 Voltage Drop | N1-VD8,N1-VD9,N1-VD10,N1-VD11,N1-VD12,N1-VD13,N1-VD14,N1-VD15,N1-VD16,N1-VD17,N1-VD18,N1-VD19,N1-VD20,N1-VD21,N1-VD22,N1-VD23,N1-VD28,N1-VD29,N1-VD30,N1-VD31,N1-VD36,N1-VD37,N1-VD38,N1-VD39,N1-VD40,N1-VD41,N1-VD42,N1-VD43,N1-VD44,N1-VD45,N1-VD24,N1-VD25,N1-VD26,N1-VD27,N1-VD32,N1-VD33,N1-VD34,N1-VD35 | This project consists of building a 138kV line from Dowling 138kV to Bowling Green 5. At Bowling Green 5 69kV, a 138/69 kV transformer shall be built in order to interconnect the 138kV circuit to Bowling Green 69kV
2015_1-8A | Greenfield | Northeast Transmission Development | 59.4 | Penelec | 115 | N-1 Voltage Drop; N-1-1 Voltage Drop; N-1-1 Voltage Magnitude; N-1 Thermal; Gen Deliv | N1-VD5, N1-VD6; N2-VD10,N2-VD11,N2-VD12,N2-VD13,N2-VD14,N2-VD15,N2-VD16,N2-VD17,N2-VD18,N2-VD19,N2-VD20,N2-VD21,N2-VD22,N2-VD23,N2-VD24,N2-VD25,N2-VD26,N2-VD27,N2-VD28,N2-VD29,N2-VD30,N2-VD31,N2-VD32,N2-VD33,N2-VD34,N2-VD35,N2-VD36,N2-VD37,N2-VD38,N2-VD39,N2-VD40,N2-VD54,N2-VD55,N2-VD56,N2-VD57,N2-VD58,N2-VD59,N2-VD62,N2-VD63,N2-VD64,N2-VD65,N2-VD69,N2-VD70,N2-VD71,N2-VD91,N2-VD92; N2-VM1,N2-VM2,N2-VM3,N2-VM4,N2-VM9,N2-VM26,N2-VM27,N2-VM28,N2-VM29,N2-VM30,N2-VM31,N2-VM32,N2-VM33,N2-VM34,N2-VM35,N2-VM36,N2-VM37,N2-VM38,N2-VM39,N2-VM40,N2-VM48,N2-VM49,N2-VM50,N2-VM51,N2-VM52,N2-VM53,N2-VM54,N2-VM55,N2-VM56,N2-VM57,N2-VM58,N2-VM59,N2-VM60,N2-VM61,N2-VM62,N2-VM63,N2-VM64,N2-VM77,N2-VM78,N2-VM79,N2-VM80,N2-VM81,N2-VM82; 204; 674 | Build a 138 kV line from the 138 kV Bethlen substation to a new 138/115 kV substation ("Ralphton 138 kV") interconnecting to the 115 kV Ralphton substation. Build a 115 kV line from the 115 kV Ralphton substation to the 115 kV Statler Hill substation
2015_1-8B | Greenfield | Northeast Transmission Development | 58.1 | Penelec | 115 | N-1 Voltage Drop; N-1-1 Voltage Drop; N-1-1 Voltage Magnitude; N-1 Thermal; Gen Deliv | N1-VD5, N1-VD6; N2-VD10,N2-VD11,N2-VD12,N2-VD13,N2-VD14,N2-VD15,N2-VD16,N2-VD17,N2-VD18,N2-VD19,N2-VD20,N2-VD21,N2-VD22,N2-VD23,N2-VD24,N2-VD25,N2-VD26,N2-VD27,N2-VD28,N2-VD29,N2-VD30,N2-VD31,N2-VD32,N2-VD33,N2-VD34,N2-VD35,N2-VD36,N2-VD37,N2-VD38,N2-VD39,N2-VD40,N2-VD54,N2-VD55,N2-VD56,N2-VD57,N2-VD58,N2-VD59,N2-VD62,N2-VD63,N2-VD64,N2-VD65,N2-VD69,N2-VD70,N2-VD71,N2-VD91,N2-VD92; N2-VM1,N2-VM2,N2-VM3,N2-VM4,N2-VM9,N2-VM26,N2-VM27,N2-VM28,N2-VM29,N2-VM30,N2-VM31,N2-VM32,N2-VM33,N2-VM34,N2-VM35,N2-VM36,N2-VM37,N2-VM38,N2-VM39,N2-VM40,N2-VM48,N2-VM49,N2-VM50,N2-VM51,N2-VM52,N2-VM53,N2-VM54,N2-VM55,N2-VM56,N2-VM57,N2-VM58,N2-VM59,N2-VM60,N2-VM61,N2-VM62,N2-VM63,N2-VM64,N2-VM77,N2-VM78,N2-VM79,N2-VM80,N2-VM81,N2-VM82; 204; 674 | Build a 138 kV line from the 138 kV Bethlen substation to a new 138/115 kV substation ("Stonycreek") interconnecting the Hooversville-Ralphton 115 kV line and the Hooversville-Somerset 115 kV line. Build a 115 kV line from the new 115 kV Stonycreek substation to the 115 kV Statler Hill substation
2015_1-8C | Greenfield | Northeast Transmission Development | 23 | AEP | 138 | N-1-1 Voltage Drop; N-1-1 Voltage Magnitude; N-1-1 Thermal | N2-VD75,N2-VD76,N2-VD77,N2-VD78,N2-VD79,N2-VD80,N2-VD81,N2-VD82,N2-VD83,N2-VD84,N2-VD85,N2-VD86,N2-VD87,N2-VD88,N2-VD89,N2-VD90; N2-VM65,N2-VM66,N2-VM67,N2-VM68,N2-VM69; N2-T4,N2-T5,N2-T6,N2-T7,N2-T8,N2-T9,N2-T10,N2-T11,N2-T12,N2-T13,N2-T14,N2-T15 | Build a new 138 kV line interconnecting the 138 kV Bolt substation to the 138 kV Tams Mountain substation
2015_1-8D | Greenfield | Northeast Transmission Development | 20.6 | ATSI | 69 | N-1 Voltage Drop | N1-VD8,N1-VD9,N1-VD10,N1-VD11,N1-VD12,N1-VD13,N1-VD14,N1-VD15,N1-VD16,N1-VD17,N1-VD18,N1-VD19,N1-VD20,N1-VD21,N1-VD22,N1-VD23,N1-VD24,N1-VD25,N1-VD26,N1-VD27,N1-VD28,N1-VD29,N1-VD30,N1-VD31,N1-VD32,N1-VD33,N1-VD34,N1-VD35,N1-VD36,N1-VD37,N1-VD38,N1-VD39,N1-VD40,N1-VD41,N1-VD42,N1-VD43,N1-VD44,N1-VD45 | Build a double circuit 138 kV line from the Lemoyne-West End Fostoria 138 kV line to a new 138/69 kV substation ("Bowling Green 4 138 kV") and interconnecting to the Bowling Green 4 69 kV substation
2015_1-8E | Greenfield | Northeast Transmission Development | 13.2 | ATSI | 69 | N-1 Voltage Drop | N1-VD8,N1-VD9,N1-VD10,N1-VD11,N1-VD12,N1-VD13,N1-VD14,N1-VD15,N1-VD16,N1-VD17,N1-VD18,N1-VD19,N1-VD20,N1-VD21,N1-VD22,N1-VD23,N1-VD24,N1-VD25,N1-VD26,N1-VD27,N1-VD28,N1-VD29,N1-VD30,N1-VD31,N1-VD32,N1-VD33,N1-VD34,N1-VD35,N1-VD36,N1-VD37,N1-VD38,N1-VD39,N1-VD40,N1-VD41,N1-VD42,N1-VD43,N1-VD44,N1-VD45 | Build a 138 kV line from the Lemoyne-West End Fostoria 138 kV line to a new 138/69 kV substation ("Bowling Green 4 138 kV") and interconnecting to the Bowling Green 4 69 kV substation
2015_1-8F | Greenfield | Northeast Transmission Development | 45.3 | Penelec | 115 | N-1 Voltage Drop; N-1-1 Voltage Drop; N-1-1 Voltage Magnitude | N1-VD7; N2-VD5,N2-VD6,N2-VD7,N2-VD8,N2-VD9,N2-VD41,N2-VD42,N2-VD43,N2-VD44,N2-VD45,N2-VD48,N2-VD49,N2-VD50,N2-VD51,N2-VD52; N2-VM11,N2-VM14,N2-VM15,N2-VM16,N2-VM17,N2-VM18,N2-VM19,N2-VM20,N2-VM21,N2-VM22,N2-VM23,N2-VM24,N2-VM25 | Build a new 115 kV line interconnecting a new 115 kV switching station ("CherryTree") to a new 115 kV switching station ("Franklin")
2015_1-8G | Greenfield | Northeast Transmission Development | 45.3 | Penelec | 115 | N-1 Voltage Drop; N-1-1 Voltage Drop; N-1-1 Voltage Magnitude | N1-VD7; N2-VD5,N2-VD6,N2-VD7,N2-VD8,N2-VD9,N2-VD41,N2-VD42,N2-VD43,N2-VD44,N2-VD45,N2-VD48,N2-VD49,N2-VD50,N2-VD51,N2-VD52; N2-VM11,N2-VM14,N2-VM15,N2-VM16,N2-VM17,N2-VM18,N2-VM19,N2-VM20,N2-VM21,N2-VM22,N2-VM23,N2-VM24,N2-VM25 | Build a new 115 kV line interconnecting a new 115 kV switching station ("CherryTree") to the 115 kV Morgan Street substation
2015_1-8H | Greenfield | Northeast Transmission Development | 29.9 | Penelec | 115 | N-1 Voltage Drop; N-1-1 Voltage Drop; N-1-1 Voltage Magnitude | N1-VD7; N2-VD5,N2-VD6,N2-VD7,N2-VD8,N2-VD9,N2-VD41,N2-VD42,N2-VD43,N2-VD44,N2-VD45,N2-VD48,N2-VD49,N2-VD50,N2-VD51,N2-VD52; N2-VM11,N2-VM14,N2-VM15,N2-VM16,N2-VM17,N2-VM18,N2-VM19,N2-VM20,N2-VM21,N2-VM22,N2-VM23,N2-VM24,N2-VM25 | Build a new 115 kV line interconnecting a new 115 kV switching station ("CherryTree") to the 115 kV Wayne substation
2015_1-8I | Greenfield | Northeast Transmission Development | 17.1 | JCPL | 230 | N-1 Voltage Drop; N-1 Voltage Magnitude; N-1-1 Voltage drop; N-1-1 Voltage magnitude | N1-VD1; N1-VM1; N2-VD2, N2-VD3, N2-VD4; N2-VM5,N2-VM6,N2-VM7,N2-VM8,N2-VM10,N2-VM12,N2-VM13 | Build a double circuit 115 kV line from the Wyckoff-Englishtown 115 kV line to a new 230/115 kV substation ("East Windsor 115 kV") and interconnecting to the East Windsor 230 kV substation
2015_1-8J | Greenfield | Northeast Transmission Development | 26 | JCPL | 230 | N-1 Voltage Drop; N-1 Voltage Magnitude; N-1-1 Voltage drop; N-1-1 Voltage magnitude | N1-VD1; N1-VM1; N2-VD2, N2-VD3, N2-VD4; N2-VM5,N2-VM6,N2-VM7,N2-VM8,N2-VM10,N2-VM12,N2-VM13 | Build a 500/230 kV substation ("Englishtown 500 kV") interconnecting the Deans-Smithburg 500 kV line to the Englishtown 230 kV substation
2015_1-8K | Greenfield | Northeast Transmission Development | 21.5 | Penelec | 115 | N-1-1 Voltage Drop | N2-VD46,N2-VD47,N2-VD53,N2-VD60,N2-VD61,N2-VD72 | Build a 115 kV line from the existing 138 kV Grand Point substation to the existing 115 kV Carlisle Pike substation
2015_1-8L | Greenfield | Northeast Transmission Development | 22.2 | Penelec | 115 | N-1-1 Voltage Drop | N2-VD46,N2-VD47,N2-VD53,N2-VD60,N2-VD61,N2-VD72 | Build a 138 kV line from the existing 138 kV Grand Point substation to the existing 115 kV Carlisle Pike substation
2015_1-8M | Greenfield | Northeast Transmission Development | 21.7 | Penelec | 115 | N-1-1 Voltage Drop | N2-VD46,N2-VD47,N2-VD53,N2-VD60,N2-VD61,N2-VD72 | Build a 115 kV line from the existing 138 kV Grand Point substation to the existing 115 kV Roxbury substation
2015_1-8N | Greenfield | Northeast Transmission Development | 22.3 | Penelec | 115 | N-1-1 Voltage Drop | N2-VD46,N2-VD47,N2-VD53,N2-VD60,N2-VD61,N2-VD72 | Build a 138 kV line from the existing 138 kV Grand Point substation to the existing 115 kV Roxbury substation
2015_1-8O | Greenfield | Northeast Transmission Development | 45.3 | Penelec | 115 | N-1 Voltage Drop; N-1-1 Voltage Drop; N-1-1 Voltage Magnitude | N1-VD7; N2-VD5,N2-VD6,N2-VD7,N2-VD8,N2-VD9,N2-VD41,N2-VD42,N2-VD43,N2-VD44,N2-VD45,N2-VD48,N2-VD49,N2-VD50,N2-VD51,N2-VD52; N2-VM11,N2-VM14,N2-VM15,N2-VM16,N2-VM17,N2-VM18,N2-VM19,N2-VM20,N2-VM21,N2-VM22,N2-VM23,N2-VM24,N2-VM25 | Build a new 115 kV line interconnecting the 115 kV Grandview substation to a new 115 kV switching station ("Franklin")
2015_1-8P | Greenfield | Northeast Transmission Development | 45.4 | Penelec | 115 | N-1 Voltage Drop; N-1-1 Voltage Drop; N-1-1 Voltage Magnitude | N1-VD7; N2-VD5,N2-VD6,N2-VD7,N2-VD8,N2-VD9,N2-VD41,N2-VD42,N2-VD43,N2-VD44,N2-VD45,N2-VD48,N2-VD49,N2-VD50,N2-VD51,N2-VD52; N2-VM11,N2-VM14,N2-VM15,N2-VM16,N2-VM17,N2-VM18,N2-VM19,N2-VM20,N2-VM21,N2-VM22,N2-VM23,N2-VM24,N2-VM25 | Build a new 115 kV line interconnecting the 115 kV Grandview substation to the 115 kV Morgan Street substation
2015_1-8Q | Greenfield | Northeast Transmission Development | 30 | Penelec | 115 | N-1 Voltage Drop; N-1-1 Voltage Drop; N-1-1 Voltage Magnitude | N1-VD7; N2-VD5,N2-VD6,N2-VD7,N2-VD8,N2-VD9,N2-VD41,N2-VD42,N2-VD43,N2-VD44,N2-VD45,N2-VD48,N2-VD49,N2-VD50,N2-VD51,N2-VD52; N2-VM11,N2-VM14,N2-VM15,N2-VM16,N2-VM17,N2-VM18,N2-VM19,N2-VM20,N2-VM21,N2-VM22,N2-VM23,N2-VM24,N2-VM25 | Build a new 115 kV line interconnecting the 115 kV Grandview substation to the 115 kV Wayne substation
2015_1-8R | Greenfield | Northeast Transmission Development | 7.4 | AEP | 138 | N-1-1 Voltage Drop; N-1-1 Voltage Magnitude; N-1-1 Thermal | N2-VD73, N2-VD74; N2-VM70,N2-VM71,N2-VM72,N2-VM73,N2-VM74,N2-VM75,N2-VM76; N2-T16, N2-T17 | Build a 138 kV switching station ("Grassy Creek") interconnecting the Summerfield-Switzer 138 kV line, the Steamtown Skid-Natrium 138 kV line and the Tap to Somerton 138 kV line
2015_1-8S | Greenfield | Northeast Transmission Development | 15.6 | Dominion | 230 | Gen Deliv | NEW-32, NEW-34, NEW-36, NEW-37 | Build a 230 kV switching station ("Great Branch") interconnecting the Chesterfield-Iron Bridge 230 kV line, the Chesterfield-Basin 230 kV line and the Iron Bridge-Spruance 230 kV line
2015_1-8T | Greenfield | Northeast Transmission Development | 16.9 | Penelec | 115 | N-1-1 Voltage Drop | N2-VD46,N2-VD47,N2-VD53,N2-VD60,N2-VD61,N2-VD72 | Build a 115 kV line from the proposed 500/138 kV Green Ridge substation to the existing 115 kV Carlisle Pike substation
2015_1-8U | Greenfield | Northeast Transmission Development | 32.3 | Penelec | 115 | N-1-1 Voltage Drop | N2-VD46,N2-VD47,N2-VD53,N2-VD60,N2-VD61,N2-VD72 | Build a 115 kV line from the existing 115 kV Mountain substation to the existing 115 kV Carlisle Pike substation
2015_1-8V | Greenfield | Northeast Transmission Development | 19.6 | ATSI | 138 | N-1-1 Thermal | N2-T1, N2-T2, N2-T3 | Build a 138 kV line from the existing 138 kV Newton Falls substation to the existing 138 kV Franklin substation
2015_1-8W | Greenfield | Northeast Transmission Development | 29.4 | Dominion | 230 | Gen Deliv | NEW-32, NEW-34, NEW-36, NEW-37 | Build a 230 kV switching station (Great Branch) interconnecting the Chesterfield-Iron Bridge 230 kV line, the Chesterfield-Basin 230 kV line and the Iron Bridge-Spruance 230 kV line. Build a 230 kV switching station (Reedy Creek) interconnecting the Iron Bridge-Southwest 230 kV line, the Iron Bridge-Hull Street Road 230 kV line and the Hull Street Road-Southwest 230 kV line
2015_1-8X | Greenfield | Northeast Transmission Development | 78.7 | Dominion | 500 | Gen Deliv | NEW-52 | Build a 500 kV line from the 500 kV Rogers Road switching station to the existing 500 kV Carson substation
2015_1-8Y | Greenfield | Northeast Transmission Development | 27.8 | Dominion | 500 | Gen Deliv | NEW-52 | Build a 230 kV line from the new 500/230 kV substation (Rogers Road 230 kV) to the existing 230 kV Clubhouse substation
2015_1-8Z | Greenfield | Northeast Transmission Development | 19.2 | AEP | 138 | N-1-1 Voltage Drop; N-1-1 Voltage Magnitude; N-1-1 Thermal | N2-VD75,N2-VD76,N2-VD77,N2-VD78,N2-VD79,N2-VD80,N2-VD81,N2-VD82,N2-VD83,N2-VD84,N2-VD85,N2-VD86,N2-VD87,N2-VD88,N2-VD89,N2-VD90; N2-VM65,N2-VM66,N2-VM67,N2-VM68,N2-VM69; N2-T4,N2-T5,N2-T6,N2-T7,N2-T8,N2-T9,N2-T10,N2-T11,N2-T12,N2-T13,N2-T14,N2-T15 | Build a 345/138 kV substation (Sand Branch) interconnecting the Kanawha River-Matt Funk 345 kV line, the Bradley-Dameron 138 kV line and the Bradley-Pole Yard 138 kV line
2015_1-8AA | Greenfield | Northeast Transmission Development | 12 | ATSI | 138 | N-1 Voltage Drop; N-1 Voltage Magnitude | N1-VD2, N1-VD3; N1-VM2,N1-VM3,N1-VM4,N1-VM5,N1-VM6,N1-VM7,N1-VM8,N1-VM9,N1-VM10,N1-VM11,N1-VM12,N1-VM13 | Build a 138 kV switching station ("Stony Hill") interconnecting the Shenango-Masury 138 kV line, the Shenango-LTV Steel 138 kV line and the Lincoln Park-Elwood 138 kV line
2015_1-8AB | Greenfield | Northeast Transmission Development | 6 | ATSI | 138 | N-1 Voltage Drop; N-1 Voltage Magnitude | N1-VD2, N1-VD3; N1-VM2,N1-VM3,N1-VM4,N1-VM5,N1-VM6,N1-VM7,N1-VM8,N1-VM9,N1-VM10,N1-VM11,N1-VM12,N1-VM13 | Build a 138 kV switching station ("Stony Hill") interconnecting the Shenango-Masury 138 kV line and the Lincoln Park-Elwood 138 kV line
2015_1-8AC | Greenfield | Northeast Transmission Development | 6 | ATSI | 138 | N-1 Voltage Drop; N-1 Voltage Magnitude | N1-VD2, N1-VD3; N1-VM2,N1-VM3,N1-VM4,N1-VM5,N1-VM6,N1-VM7,N1-VM8,N1-VM9,N1-VM10,N1-VM11,N1-VM12,N1-VM13 | Build a 138 kV switching station ("Stony Hill") interconnecting the Shenango-LTV Steel 138 kV line and the Lincoln Park-Elwood 138 kV line
2015_1-8AD | Greenfield | Northeast Transmission Development | 19.4 | ATSI | 138 | N-1-1 Thermal | N2-T1, N2-T2, N2-T3 | Build a double circuit 138 kV line from the Central Niles-Garden 138 kV line to a new switching station ("Wick") on the Masury-Salt Springs 138 kV line
2015_1-9A | Greenfield | ITC | 167.1 | Dominion | 500 | Gen Deliv | NEW-32, NEW-34, NEW-36, NEW-37, NEW-52 | Construct a new 500 kV line connecting the existing Rawlings 500 kV switchyard and the existing Midlothian 500 kV substation. Upgrade the existing Rawlings switchyard and Midlothian substation to accommodate the new 500 kV line.
2015_1-9B | Greenfield | ITC | 118.9 | Dominion | 500;230 | Gen Deliv | NEW-52, NEW-32, NEW-36 | Construct a new 500 kV line from the existing Rawlings 500 kV switchyard to a new switchyard (Lakeland) which taps the existing Carson-Midlothian 500 kV line
2015_1-9C | Greenfield | ITC | 105.7 | Dominion | 500;230 | Gen Deliv | NEW-52, NEW-A | Construct a new 500 kV line from the existing Rawlings 500 kV switchyard to a new switchyard (Steers) which taps the existing Carson-Midlothian 500 kV line
2015_1-9D | Greenfield | ITC | 135.2 | Dominion | 500;230 | Gen Deliv | NEW-52, NEW-32, NEW-36 | Construct a new 500 kV line from the existing Brunswick 500 kV switchyard to the existing Carson 500 kV substation. Upgrade the existing Brunswick Switchyard and Carson Substation to accommodate the new 500 kV line
2015_1-9E | Greenfield | ITC | 94.2 | Dominion | 500;230 | Gen Deliv | NEW-52, NEW-32, NEW-36 | Construct a new 500 kV line from the existing Rawlings 500 kV switchyard to the existing Carson 500 kV substation. Upgrade the existing Rawlings Switchyard and Carson Substation to accommodate the new 500 kV line